## BOG
Location: |  | Tbilisi, Gagarini str.29
Chiller technical specification
| 1 | Operation conditions:
| a. | Summer Outlet Air Condition: | +38 ⁰C (DB) 30% RH
| b. | Winter Outlet Air Condition: | -8 ⁰C (DB) 70% RH
| 2 | General information:
| a. | Equipment Location | Outdoor
| b. | Type: | Cooling only chiller (Air-cooled)
| c. | Designation | CH-01 (1 unit)
| 3 | Cooling capacity:
| a. | MIN Cooling Capacity (kW) | 800
| b. | MAX Cooling Capacity (kW) | 1000
| c. | Water Inlet Temperature (⁰C) | 12
| d. | Water Outlet Temperature (⁰C) | 7
| 4 | Refrigerant/Chilled Fluid:
| a. | The chiller uses plain water (100% water) as the chilled fluid in the system — no glycol or other additives mixed in the chilled water circuit | 100% water
| b. | Refrigerant type: Note:The chiller shall use refrigerant R410A, consistent with the existing installed chillers | R410A
| 5 | Compressor:
| a. | Type: | Scroll, Fixed-frequency
| b. | Capacity control: | Min. 4-step Stage capacity control
| c. | Circuit quantity: | 2 independent refrigerant circuits
| 6 | Energy efficiency:
| a. | EER (energy efficianty class B or higher) | EER ≥ 2.9
| 7 | Electrical Data:
| a. | Voltage/Phase/Frequency: | 400V / 3 Phase / 50 Hz
| 8 | Controls & Integration:
| a. | Integrated Hydromodule:Integrated with a single circulation pump, expansion tank, safety valves, pressure gauges, and flow control devices
| b. | BMS Integration: | BACnet/Modbus
| 9 | Scope of Suplly:
| a. | Supply of chiller unit as specified
| b. | Deinstallation of existing chiller
| c. | Installation of new chiller at site
| d. | Transportation of secondary chiller to warehouse
| e. | Testing and commissioning including performance verification, electrical tests, and BMS integration check
| 10 | Documentation:
| a. | Operation and maintenance manual
| b. | Spare parts list
| c. | Warranty conditions (specify duration)