## IO
| INSTRUMENT_TAG | PLC_TAG | DESCRIPTION | SIGNAL_TYPE |  | RANGE | POWER_SUPPLY
RIO cabinet | SW_LIT_001 |  | Sour Water Feed Tank Level Control | AI | 4-20 mA | 0 - 100 % | 24VDC | 2-wire connection, instrument is passive
| SW_FIT_001 |  | Sour water to reactor SW-RT-001 | AI | 4-20 mA | 0 - 150 m3/hr | 24VDC | 2-wire 4-20 mA connection (Instrument is active); Pulse output (2-wire connection); 2-wire power supply 24 V DC.
|  |  | Sour water to reactor SW-RT-001 (Totalizer) | DI | RIO is active | 1 pulse - 0.05 m3 | 24VDC
[5 empty] | 24 V DC power supply |  | 24VDC
| SW_FIT_002 |  | Sour water to reactor SW-RT-002 | AI | 4-20 mA | 0 - 150 m3/hr | 24VDC | 2-wire 4-20 mA connection (Instrument is active); Pulse output (2-wire connection); 2-wire power supply 24 V DC.
|  |  | Sour water to reactor SW-RT-002 (Totalizer) | DI | RIO is active | 1 pulse - 0.05 m3 | 24VDC
[5 empty] | 24 V DC power supply |  | 24VDC
| SW_FIT_003 |  | Sour water to reactor SW-RT-003 | AI | 4-20 mA | 0 - 150 m3/hr | 24VDC | 2-wire 4-20 mA connection (Instrument is active); Pulse output (2-wire connection); 2-wire power supply 24 V DC.
|  |  | Sour water to reactor SW-RT-003 (Totalizer) | DI | RIO is active | 1 pulse - 0.05 m3 | 24VDC
[5 empty] | 24 V DC power supply |  | 24VDC
| SW_FIT_004 |  | Sour water to reactor SW-RT-004 | AI | 4-20 mA | 0 - 150 m3/hr | 24VDC | 2-wire 4-20 mA connection (Instrument is active); Pulse output (2-wire connection); 2-wire power supply 24 V DC.
|  |  | Sour water to reactor SW-RT-004 (Totalizer) | DI | RIO is active | 1 pulse - 0.05 m3 | 24VDC
[5 empty] | 24 V DC power supply |  | 24VDC
| SW_PU_001_M01 |  | Sour Water Line 1 To Reactor SW-RT-001 | Digital | Ethernet IP | 0 - 1500 RPM, VFD | - | Control by communication. Outputs: Start, Stop, Setpoint Inputs: Working, Stopped, Feedback, Faulted
| SW_PU_002_M01 |  | Sour Water Line 2 To Reactor SW-RT-002 | Digital | Ethernet IP | 0 - 1500 RPM, VFD | - | Control by communication. Outputs: Start, Stop, Setpoint Inputs: Working, Stopped, Feedback, Faulted
| SW_PU_003_M01 |  | Sour Water Line 3 To Reactor SW-RT-003 | Digital | Ethernet IP | 0 - 1500 RPM, VFD | - | Control by communication. Outputs: Start, Stop, Setpoint Inputs: Working, Stopped, Feedback, Faulted
| SW_PU_004_M01 |  | Sour Water Line 4 To Reactor SW-RT-004 | Digital | Ethernet IP | 0 - 1500 RPM, VFD | - | Control by communication. Outputs: Start, Stop, Setpoint Inputs: Working, Stopped, Feedback, Faulted
P L C C a b I n e t | WT3_PH_001 |  | PH Control | AI | 4-20 mA | - | 24VDC 220 VAC | 2-wire connection, instrument is passive Power Supply for the transmitter is 220 V AC
| WT3_LIT_001 |  | Lime Milk Tank Level Control | AI | 4-20 mA | 0 - 100 % | 24VDC | 2-wire connection, instrument is passive
| WT3-LIT-001 |  | Overflow Tank Level Control | AI | 4-20 mA | 0 - 100 % | 24VDC | 2-wire connection, instrument is passive
| WT3_FIT_001 |  | Lime Milk To WT3-RT-001 (Line 1) | AI | 4-20 mA | 0 - 200 m3/hr | 24VDC | 2-wire 4-20 mA connection (Instrument is active); Pulse output (2-wire connection); 2-wire power supply 24 V DC.
|  |  | Lime Milk To WT3-RT-001 (Totalizer) | DI | RIO is active | 1 pulse - 0.05 m3 | 24VDC
[5 empty] | 24 V DC power supply |  | 24VDC
| WT3_FIT_002 |  | Lime Milk To WT3-RT-001 (Line 2) | AI | 4-20 mA | 0 - 200 m3/hr | 24VDC | 2-wire 4-20 mA connection (Instrument is active); Pulse output (2-wire connection); 2-wire power supply 24 V DC.
|  |  | Lime Milk To WT3-RT-001 (Totalizer) | DI | RIO is active | 1 pulse - 0.05 m3 | 24VDC
[5 empty] | 24 V DC power supply |  | 24VDC
| WT3_FIT_003_1 |  | Flocculant to Thickener N3 | AI | 4-20 mA | 0 - 2 m3/hr | 24VDC | 2-wire 4-20 mA connection (Instrument is active); Pulse output (2-wire connection); 2-wire power supply 24 V DC.
|  |  | Flocculant to Thickener N3 (Totalizer) | DI | RIO is active | 1 pulse - 0.005 m3 | 24VDC
[5 empty] | 24 V DC power supply |  | 24VDC
| WT3_FIT_003_2 |  | Flocculant to Thickener N4 | AI | 4-20 mA | 0 - 2 m3/hr | 24VDC | 2-wire 4-20 mA connection (Instrument is active); Pulse output (2-wire connection); 2-wire power supply 24 V DC.
|  |  | Flocculant to Thickener N4 (Totalizer) | DI | RIO is active | 1 pulse - 0.005 m3 | 24VDC
[5 empty] | 24 V DC power supply |  | 24VDC
| WT3_FIT_003_3 |  | Flocculant to Thickener N5 | AI | 4-20 mA | 0 - 2 m3/hr | 24VDC | 2-wire 4-20 mA connection (Instrument is active); Pulse output (2-wire connection); 2-wire power supply 24 V DC.
|  |  | Flocculant to Thickener N5 (Totalizer) | DI | RIO is active | 1 pulse - 0.005 m3 | 24VDC
[5 empty] | 24 V DC power supply |  | 24VDC
| WT3_FIT_003_4 |  | Flocculant to Thickener N6 | AI | 4-20 mA | 0 - 2 m3/hr | 24VDC | 2-wire 4-20 mA connection (Instrument is active); Pulse output (2-wire connection); 2-wire power supply 24 V DC.
|  |  | Flocculant to Thickener N6 (Totalizer) | DI | RIO is active | 1 pulse - 0.005 m3 | 24VDC
[5 empty] | 24 V DC power supply |  | 24VDC
| WT3_PIT_003_1 |  | Flocculant Pressure Control to Thickener N1 | AI | 4-20 mA | 24VDC | 24VDC | 2-wire connection, instrument is passive
| WT3_PIT_003_2 |  | Flocculant Pressure Control to Thickener N2 | AI | 4-20 mA | 24VDC | 24VDC | 2-wire connection, instrument is passive
| WT3_PIT_003_3 |  | Flocculant Pressure Control to Thickener N3 | AI | 4-20 mA | 24VDC | 24VDC | 2-wire connection, instrument is passive
| WT3_PIT_003_4 |  | Flocculant Pressure Control to Thickener N4 | AI | 4-20 mA | 24VDC | 24VDC | 2-wire connection, instrument is passive
| WT3_BV007_3_sp |  | WT3_BV007_3 Setpoint | AO | 4-20 mA | Power supply for the valve is 24 V DC | 24VDC | 2-wire connection valve is passive
| WT3_BV007_3_fb |  | WT3_BV007_3 Feedback | AI | 4-20 mA |  | 24VDC | 2-wire connection valve is active
| WT3_BV007_4_sp |  | WT3_BV007_4 Setpoint | AO | 4-20 mA | Power supply for the valve is 24 V DC | 24VDC | 2-wire connection valve is passive
| WT3_BV007_4_fb |  | WT3_BV007_4 Feedback | AI | 4-20 mA |  | 24VDC | 2-wire connection valve is active
| WT3_BV007_5_sp |  | WT3_BV007_5 Setpoint | AO | 4-20 mA | Power supply for the valve is 24 V DC | 24VDC | 2-wire connection valve is passive
| WT3_BV007_5_fb |  | WT3_BV007_5 Feedback | AI | 4-20 mA |  | 24VDC | 2-wire connection valve is active
| WT3_BV007_6_sp |  | WT3_BV007_6 Setpoint | AO | 4-20 mA | Power supply for the valve is 24 V DC | 24VDC | 2-wire connection valve is passive
| WT3_BV007_6_fb |  | WT3_BV007_6 Feedback | AI | 4-20 mA |  | 24VDC | 2-wire connection valve is active
| WT3_FIT_004_1 |  | Neutrilized Water to Thickener N3 | AI | 4-20 mA | 0 - 150 m3/hr | 24VDC | 2-wire 4-20 mA connection (Instrument is active); Pulse output (2-wire connection); 2-wire power supply 24 V DC.
|  |  | Neutrilized Water to Thickener N3 (Totalizer) | DI | RIO is active | 1 pulse - 0.05 m3 | 24VDC
[5 empty] | 24 V DC power supply |  | 24VDC
| WT3_FIT_004_2 |  | Neutrilized Water to Thickener N4 | AI | 4-20 mA | 0 - 150 m3/hr | 24VDC | 2-wire 4-20 mA connection (Instrument is active); Pulse output (2-wire connection); 2-wire power supply 24 V DC.
|  |  | Neutrilized Water to Thickener N4 (Totalizer) | DI | RIO is active | 1 pulse - 0.05 m3 | 24VDC
[5 empty] | 24 V DC power supply |  | 24VDC
| WT3_FIT_004_3 |  | Neutrilized Water to Thickener N5 | AI | 4-20 mA | 0 - 150 m3/hr | 24VDC | 2-wire 4-20 mA connection (Instrument is active); Pulse output (2-wire connection); 2-wire power supply 24 V DC.
|  |  | Neutrilized Water to Thickener N5 (Totalizer) | DI | RIO is active | 1 pulse - 0.05 m3 | 24VDC
[5 empty] | 24 V DC power supply |  | 24VDC
| WT3_FIT_004_4 |  | Neutrilized Water to Thickener N6 | AI | 4-20 mA | 0 - 150 m3/hr | 24VDC | 2-wire 4-20 mA connection (Instrument is active); Pulse output (2-wire connection); 2-wire power supply 24 V DC.
|  |  | Neutrilized Water to Thickener N6 (Totalizer) | DI | RIO is active | 1 pulse - 0.05 m3 | 24VDC
[5 empty] | 24 V DC power supply |  | 24VDC
| WT3_FIT_005 |  | Sour Water 2nd type To Reactor WT3-RT-001 | AI | 4-20 mA | 0 - 150 m3/hr | 24VDC | 2-wire 4-20 mA connection (Instrument is active); Pulse output (2-wire connection); 2-wire power supply 24 V DC.
|  |  | Sour Water 2nd type To Reactor WT3-RT-001 (Totalizer) | DI | RIO is active | 1 pulse - 0.05 m3 | 24VDC
[5 empty] | 24 V DC power supply |  | 24VDC
| SW_FIT_006 |  | Sour Water To Reactor WT3-RT-001 | AI | 4-20 mA | 0 - 150 m3/hr | 24VDC | 2-wire 4-20 mA connection (Instrument is active); Pulse output (2-wire connection); 2-wire power supply 24 V DC.
|  |  | Sour Water To Reactor WT3-RT-001 (Totalizer) | DI | RIO is active | 1 pulse - 0.05 m3 | 24VDC
[5 empty] | 24 V DC power supply |  | 24VDC
| SW3_FIT_008 |  | Overflow Tank Flow Control Line 1 | AI | 4-20 mA | 0 - 150 m3/hr | 24VDC | 2-wire 4-20 mA connection (Instrument is active); Pulse output (2-wire connection); 2-wire power supply 24 V DC.
|  |  | Overflow Tank Flow Control Line 1 (Totalizer) | DI | RIO is active | 1 pulse - 0.05 m3 | 24VDC
[5 empty] | 24 V DC power supply |  | 24VDC
| SW3_FIT_009 |  | Overflow Tank Flow Control Line 2 | AI | 4-20 mA | 0 - 150 m3/hr | 24VDC | 2-wire 4-20 mA connection (Instrument is active); Pulse output (2-wire connection); 2-wire power supply 24 V DC.
|  |  | Overflow Tank Flow Control Line 2 (Totalizer) | DI | RIO is active | 1 pulse - 0.05 m3 | 24VDC
[5 empty] | 24 V DC power supply |  | 24VDC
| WT3_HV_004_1 |  | Neutrilized Water Pneumatic Valve to Thickener N3 | DI | Dry contact |  | 24VDC | Closed Status | pneumatic actuated, 2-coils solenoid, 2 mechanical limit switches
|  |  | Neutrilized Water Pneumatic Valve to Thickener N3 | DI | Dry contact |  | 24VDC | Opened Status
|  |  | Neutrilized Water Pneumatic Valve to Thickener N3 | DO | + 24 V from module |  | 24VDC | Close Command active output +24VDC
|  |  | Neutrilized Water Pneumatic Valve to Thickener N3 | DO | + 24 V from module |  | 24VDC | Close Command active output +24VDC
| WT3_HV_004_2 |  | Neutrilized Water Pneumatic Valve to Thickener N4 | DI | Dry contact |  | 24VDC | Closed Status | pneumatic actuated, 2-coils solenoid, 2 mechanical limit switches
|  |  | Neutrilized Water Pneumatic Valve to Thickener N4 | DI | Dry contact |  | 24VDC | Opened Status
|  |  | Neutrilized Water Pneumatic Valve to Thickener N4 | DO | + 24 V from module |  | 24VDC | Close Command active output +24VDC
|  |  | Neutrilized Water Pneumatic Valve to Thickener N4 | DO | + 24 V from module |  | 24VDC | Close Command active output +24VDC
| WT3_HV_004_3 |  | Neutrilized Water Pneumatic Valve to Thickener N5 | DI | Dry contact |  | 24VDC | Closed Status | pneumatic actuated, 2-coils solenoid, 2 mechanical limit switches
|  |  | Neutrilized Water Pneumatic Valve to Thickener N5 | DI | Dry contact |  | 24VDC | Opened Status
|  |  | Neutrilized Water Pneumatic Valve to Thickener N5 | DO | + 24 V from module |  | 24VDC | Close Command active output +24VDC
|  |  | Neutrilized Water Pneumatic Valve to Thickener N5 | DO | + 24 V from module |  | 24VDC | Close Command active output +24VDC
| WT3_HV_004_4 |  | Neutrilized Water Pneumatic Valve to Thickener N6 | DI | Dry contact |  | 24VDC | Closed Status | pneumatic actuated, 2-coils solenoid, 2 mechanical limit switches
|  |  | Neutrilized Water Pneumatic Valve to Thickener N6 | DI | Dry contact |  | 24VDC | Opened Status
|  |  | Neutrilized Water Pneumatic Valve to Thickener N6 | DO | + 24 V from module |  | 24VDC | Close Command active output +24VDC
|  |  | Neutrilized Water Pneumatic Valve to Thickener N6 | DO | + 24 V from module |  | 24VDC | Close Command active output +24VDC
| WT3_PU_007_M01 |  | Lime Milk Dosing Pump 1 | Digital | Ethernet IP | 0 - 1500 RPM, VFD | - | Control by communication. Outputs: Start, Stop, Setpoint Inputs: Working, Stopped, Feedback, Faulted
| WT3_PU_008_M01 |  | Lime Milk Dosing Pump 2 | Digital | Ethernet IP | 0 - 1500 RPM, VFD | - | Control by communication. Outputs: Start, Stop, Setpoint Inputs: Working, Stopped, Feedback, Faulted
| WT1_PU003_M01 |  | Thickener N3 Underflow Pump 1 | Digital | Ethernet IP | 0 - 1500 RPM, VFD | - | Control by communication. Outputs: Start, Stop, Setpoint Inputs: Working, Stopped, Feedback, Faulted
| WT1_PU004_M01 |  | Thickener N3 Underflow Pump 2 | Digital | Ethernet IP | 0 - 1500 RPM, VFD | - | Control by communication. Outputs: Start, Stop, Setpoint Inputs: Working, Stopped, Feedback, Faulted
| WT2_PU003_M01 |  | Thickener N4 Underflow Pump 1 | Digital | Ethernet IP | 0 - 1500 RPM, VFD | - | Control by communication. Outputs: Start, Stop, Setpoint Inputs: Working, Stopped, Feedback, Faulted
| WT2_PU004_M01 |  | Thickener N4 Underflow Pump 2 | Digital | Ethernet IP | 0 - 1500 RPM, VFD | - | Control by communication. Outputs: Start, Stop, Setpoint Inputs: Working, Stopped, Feedback, Faulted
| WT3_PU003_M01 |  | Thickener N5 Underflow Pump 1 | Digital | Ethernet IP | 0 - 1500 RPM, VFD | - | Control by communication. Outputs: Start, Stop, Setpoint Inputs: Working, Stopped, Feedback, Faulted
| WT3_PU004_M01 |  | Thickener N5 Underflow Pump 2 | Digital | Ethernet IP | 0 - 1500 RPM, VFD | - | Control by communication. Outputs: Start, Stop, Setpoint Inputs: Working, Stopped, Feedback, Faulted
| WT3_PU003_1_M01 |  | Thickener N6 Underflow Pump 1 | Digital | Ethernet IP | 0 - 1500 RPM, VFD | - | Control by communication. Outputs: Start, Stop, Setpoint Inputs: Working, Stopped, Feedback, Faulted
| WT3_PU004_1_M01 |  | Thickener N6 Underflow Pump 2 | Digital | Ethernet IP | 0 - 1500 RPM, VFD | - | Control by communication. Outputs: Start, Stop, Setpoint Inputs: Working, Stopped, Feedback, Faulted
| WT3_PU005_1_M01 |  | Overflow Tank Pump 1 | Digital | Ethernet IP | 0 - 1500 RPM, VFD | - | Control by communication. Outputs: Start, Stop, Setpoint Inputs: Working, Stopped, Feedback, Faulted
| WT3_PU006_1_M01 |  | Overflow Tank Pump 2 | Digital | Ethernet IP | 0 - 1500 RPM, VFD | - | Control by communication. Outputs: Start, Stop, Setpoint Inputs: Working, Stopped, Feedback, Faulted
| SW_PU_005_M01 |  | Sour Water Line 1 To Reactor WT3-RT-001 | Digital | Ethernet IP | 0 - 1500 RPM, VFD | - | Control by communication. Outputs: Start, Stop, Setpoint Inputs: Working, Stopped, Feedback, Faulted
| SW_PU_006_M01 |  | Sour Water Line 2 To Reactor WT3-RT-001 | Digital | Ethernet IP | 0 - 1500 RPM, VFD | - | Control by communication. Outputs: Start, Stop, Setpoint Inputs: Working, Stopped, Feedback, Faulted
| WT3_MX_001_M01 |  | Mixer WT3-RT-001 | Digital | Ethernet IP | 0 - 1500 RPM, VFD | - | Control by communication. Outputs: Start, Stop, Setpoint Inputs: Working, Stopped, Feedback, Faulted
| WT3_MX_002_M01 |  | Mixer WT3-RT-002 | Digital | Ethernet IP | 0 - 1500 RPM, VFD | - | Control by communication. Outputs: Start, Stop, Setpoint Inputs: Working, Stopped, Feedback, Faulted
| WT3_SPP2_10 |  | Flocculant Unit 1 System Running | DI | Dry Contact
| WT3_SPP2_11 |  | Flocculant Unit 1 System Faulted | DI | Dry Contact
| WT3_SPP2_20 |  | Flocculant Unit 2 System Running | DI | Dry Contact
| WT3_SPP2_21 |  | Flocculant Unit 2 System Faulted | DI | Dry Contact
| WT3_PU_002_10 |  | Flocculant Dosing Pump 1 Start command | DO | + 24 V from module |  |  | DO through Relay with SPDT contact
| WT3_PU_002_11 |  | Flocculant Dosing Pump 1 Stop command | DO | + 24 V from module |  |  | DO through Relay with SPDT contact
| WT3_PU_002_12 |  | Flocculant Dosing Pump 1 Working Status | DI | Dry Contact
| WT3_PU_002_13 |  | Flocculant Dosing Pump 1 Faulted Status | DI | Dry Contact
| WT3_PU_002_20 |  | Flocculant Dosing Pump 2 Start command | DO | + 24 V from module |  |  | DO through Relay with SPDT contact
| WT3_PU_002_21 |  | Flocculant Dosing Pump 2 Stop command | DO | + 24 V from module |  |  | DO through Relay with SPDT contact
| WT3_PU_002_22 |  | Flocculant Dosing Pump 2 Working Status | DI | Dry Contact
| WT3_PU_002_23 |  | Flocculant Dosing Pump 2 Faulted Status | DI | Dry Contact