I&C Service Engineer, Ore Enrichment Plant Madneuli

Svintsov Stanislav

28 September 2025

TECHNICAL SPECIFICATION
For the procurement of a Temperature Sensor (Thermotransducer)

| Item № | Parameter Name | Value |  |
| --- | --- | --- | --- |
| 1 | Customer | I&C Service, Ore Enrichment Plant Madneuli |  |
| 2 | Full name, position, phone, e-mail of the responsible executor / Customer’s representative | Svintsov S.P.., Engineer of I&C Service |  |
|  |  | Engineer of I&C Service |  |
|  |  | +995591957961 |  |
|  |  | SSvintsov@richmetalsgroup.com |  |
| 3 | Basis for procurement | Notice of unsuitability for use |  |
| 4 | Equipment name | Temperature Sensor (Thermotransducer) |  |
| 5 | Quantity to be procured | 1 set |  |
| 6 | Technical characteristics, requirements | Measured medium characteristics: |  |
|  |  | Name | Slurry, Water, Air |
|  |  | Temperature, Со | +30…+45 |
|  |  | Excess pressure, kPa | 100 to 101,3 kPa |
|  |  | Ambient characteristics: |  |
|  |  | Temperature, Со | +10…+35 |
|  |  | Humidity, % | 60…80 |
|  |  | Aggressiveness | yes |
|  |  | Dust presence | yes |
|  |  | Flometer characteristics: |  |
|  |  | Transducer type | Temperature sensor Pt100 (compliant with IEC60751) |
|  |  | Process connection Fitting diameter; material: Neck length E: Immersion tip shape: Immersion length L: | Thread: G1 9 mm; 316L, DIN43772-2G 80 mm, DIN43772-2G Straight 160 mm |
|  |  | Power supply / Output signal | 4-20mA HART |
|  |  | Measured parameters | Liquids Air |
|  |  | Measuring range | PT100 TF StrongSens: -50 °C ...500 °C (-58 °F ...932 °F) PT100 WW: -200 °C ...600 °C (-328 °F ...1.112 °F) PT100 TF: -50 °C ...400 °C (-58 °F ...752 °F) |
|  |  | Ambient temperature range | -40°C...85°C |
|  |  | Protection rating | IP66/68 |
|  |  | Display | No |
|  |  | Connection | 4...20 мА HART PROFIBUS PA FOUNDATION Fieldbus |
| 7 | Documentation | - Availability of operation and maintenance manual (documentation language – Russian, English). - Availability of type approval certificate for measuring instruments and calibration procedure – Not required. - Availability of verification certificate (initially verified) – Not required. |  |
| 8 | Warranty period | Not less than 1 year |  |
| 9 | Additional conditions | None |  |
| 10 | Other requirements | None |  |

Approval - Non-hazardous area

Head; Cable Entry - TA30A Alu, IP66/68; M20

Pipe Diameter; Material - 9 mm; 316L, DIN43772-2G

Neck Length E - 80 mm, DIN43772-2G

Process Connection - G1 male thread, 316L

Tip Shape – Straight

Immersion Length L - 160 mm

Head Transmitter; Range - TMT180-A22 fix; 4-20mA, 0.1K; temp. range to be spec. -50/250oC

RTD; Wire; Measuring Range; Class - 1xPt100 TF; 3; -50...+400oC; A, increased vibration resistance

Material Certificate - Not needed

Test Report - Not needed

Test/Calibration - 0/ +100/+150oC, 1x RTD