Required product: Factory Made Booster set for municipal water supply 1+1 with control panel; H 110m; Q 120 m3/h for each pump

Quantity: 1 Factory Made Booster set with control panel and 100 liters expansion tank

Supervision of commissioning and start-up should be included in the price

Shaft correction should be included in the price if necessary

Total Set should include:

2 pumps + Asynchronous Motor

Frame; Suction/discharge manifold complete with flanges and check valves

Pump Control panel with Modbus RTU communication module

Expansion Tank – 100 liters

And all other necessary parts to ensure proper operation of the Booster set for municipal water supply

Requirements for pumps and motors:

Pump type: Centrifugal.

Application type: Drinking water.

Pump capacity: 120 m3/h. for each pump

Pump elevation head: 110 m.

Motor type: Asynchronous.

Voltage Rating: 0.4 Kv; 3X380VAC

Rpm: 1500/3000

Motor control: VFD

Requirement for control panel:

Required material: Booster set Control panel (Factory made)

Quantity: 1 set (according to offer pump powers)

Panel rated voltage: 0.4 Kv; 3X380VAC

Motor Control method: VFD

Communication Module: Modbus RTU

Panel Features:

- Reservoir Level control

- Soft pressure build-up (To prevent water hammer during startup).

- Pipe filling function.

- Selection of automatic pump changeover and pump

priority.

- Auto/Manual operation.

- Emergency stop button accessible on the control panel.

- Possibility of external setpoint influence.

- Log function.

- Possibility of digital remote-control functions:

- Support for communication fieldbus protocols (Modbus, Profibus, or Ethernet/IP).

- HMI

- Control Panel minimum protection type IP54.