# Technical Specifications

Modernization/Installation of the "Bagebi" Pumping Station Control and Monitoring System

# 1. Project Essence and Primary Objective

The primary goal of the project is a full review and adaptation of the existing (unimplemented) automation project, considering today's real-world circumstances.

The contractor must ensure the preparation of design changes, system assembly, installation, programming, and commissioning.

# 2. Scope of Work and Stages

## 2.1 Design Changes and Agreement

The contractor is obliged to study the power and technological equipment existing on-site (9 pump units, 6 kV cells, Soft Starters) and make relevant corrections to the old design documentation.

Important condition: All changes to the project and the control logic must be agreed upon with the company representative and confirmed in writing before work begins.

## 2.2 Hardware Provision and Installation

The control system must be built on a SOFREL S4W, LACROIX expandable RTU.

Hardware Supply: The client company will provide the contractor with SOFREL controllers and modules.

The contractor is responsible for providing all other necessary auxiliary materials (cables, sensors, panels, etc.).

The contractor must carry out the physical installation of the system and its integration with the existing infrastructure.

## 2.3 Programming and Commissioning

Software development on the SOFREL platform.

Adjustment of the automatic pump control algorithm based on data received from the "Tsavkisi" reservoir.

System testing and final launch.

# 3. Functional Requirements

Level Control: Continuous (analog) and emergency (float) monitoring of the water level in the reservoir.

Unit Management: Pump rotation, recording of operating hours, automatic activation of the reserve, and emergency protection.

Control Modes: Local and remote (automatic/manual).

Monitoring: Recording of electrical parameters (A, V, kW), pressure, flow, and unit statuses.

# 4. Acceptance-Handover and Documentation

After completion of the work, the contractor must submit:

Documentation: Electrical schemes and drawings reflecting the actual condition.

Software: Functional program code and configuration files (with the possibility of future modification).

Instruction: System operation manual in the Georgian language.

# 5. Warranty Terms

Work Warranty: The contractor provides a quality guarantee for the performed work (installation, connections, programming) for 36 months from the date of system acceptance into operation.

Defect Rectification: During the warranty period, in the event of an installation or software defect, the contractor is obliged to fix the problem at their own expense within 24-48 hours of receiving notification.

Hardware Warranty: Since the client provides the SOFREL controllers, the contractor is not responsible for factory defects with these devices. However, the contractor is responsible for damage caused by incorrect installation or incorrect electrical connections of the hardware.

Software Support: During the warranty period, the contractor provides software support and, if necessary, makes minor corrections to the control logic, which does not imply a fundamental reconstruction of the system.