Terms of Reference (TOR)

Gardabani Pilot Solar Sludge Dryer Remote Data Acquisition and Transfer

1. General information

Project name: Installation of an automated control system for Gardabani Pilot Solar Sludge Dryer Remote Data Acquisition and Transfer

Location of the facility: Waste Water Treatment Plant, Gardabani, Georgia

Client: Gardabani WWTP

2. Project Objective

The goal of the project is to ensure continuous, automated and remote acquisition and transmission of operational data from the Pilot Solar Sludge Dryer located in Gardabani.

The system shall collect the relevant technological parameters recorded by the dryer at defined intervals and transmit them remotely to a central server or designated data platform. The implemented solution shall eliminate the need for manual data extraction via USB devices and enable centralized storage, structured data processing and further analysis of parameter interdependencies under both normal and varying operating conditions.

3. Description of the current situation

The features of the currently operating system are:

- The Solar Sludge Dryer records operational parameters (including sludge weight, solar radiation, ambient temperature, internal temperature, humidity, ammonium concentration and other process-related data);

- Data is recorded at 2-minute intervals and stored locally in the dryer’s internal controller/system;

- Data retrieval is performed manually by physically connecting a USB storage device to the system;

- The downloaded data is transferred to a computer and processed manually in Excel for visualization and analysis;

- No remote data transmission or centralized real-time monitoring is currently implemented.

The data management approach is fully manual and does not ensure continuous remote access, systematic monitoring and timely analysis of the technological process. As a result, operational evaluation and performance optimization are delayed and dependent on physical site visits.

To eliminate the existing limitations, it is necessary to implement an automated remote data acquisition and transmission system capable of collecting the recorded parameters and transferring them to a centralized platform for storage, monitoring and further analysis.

4. Project scope

The executing company must ensure the implementation of a complete remote data acquisition and transmission system, which includes:

- System engineering analysis and development of the data integration architecture between the Solar Sludge Dryer and the Microcom RTU;

- Supply, installation and integration of the Microcom RTU and all required communication and interface components;

- The system shall provide data export functionality in Excel-compatible (xlsx) and/or CSV format, ensuring direct usability for further analysis and graphical processing.

- Commissioning of the system and delivery to the customer in fully operational condition.

5. Functional requirements

The Solar Sludge Dryer control system records the following operational parameters at 2-minute intervals and stores them locally:

- Time (timestamp);

- Sludge weight;

- Solar radiation;

- Ambient temperature;

- Internal dryer temperature;

- Internal humidity;

- External humidity;

- Ammonium concentration;

- Electricity consumption (kWh).

The implemented Microcom-based system shall ensure automatic acquisition of the above-mentioned parameters from the existing dryer control system and their remote transmission to  Zeus central data platform.

The system shall:

- Data acquisition shall be implemented in read-only mode, ensuring no impact on the control logic or operational stability of the dryer.

- Transmit the collected data at defined intervals;

- Ensure secure and continuous storage of historical records;

- Provide remote access to real-time and historical data;

- Enable export of recorded data in Excel (.xlsx) and/or CSV format for further analysis.

6. Existing Control and Transmission Devices

According to the operating instructions manual of the Solar Sludge Dryer, the control system is based on Siemens hardware and consists of the following components:

6.1. PLC and Controller Information

- PLC System: The control system is equipped with a Siemens CPU 1214C PLC (model 6ES7 214-1AG40-0XB0), which is a compact controller from the SIMATIC S7-1200 family.

- HMI / Touch Panel: The system is equipped with a Siemens KTP400 Basic touch panel for operator interface and system control.

- Heating Controller: A separate Winkler WRW-200 temperature controller is installed for control of the electric floor heating system. This controller operates independently from the main PLC system.

6.2. Communication and Data Transmission

- Available Communication Interface: The PLC provides an Ethernet interface which supports industrial network communication.

- Supported Protocols: The PLC hardware is capable of supporting industrial communication protocols such as Modbus and PROFINET over the Ethernet interface.

- USB Data Export: Operational data from the control system can be manually exported via a USB port located inside the distribution board cabinet.

- File Format: Exported data is provided in a plain text (.TXT) format, which can be imported into Microsoft Excel for further processing and analysis.

7. Submission and acceptance

- The system must be delivered in a fully operational, stable and functional state;

- A test run must be carried out in real technological mode;

- Prepare a basic electrical diagram of the control panel.

8. Warranty Terms

- Workmanship Warranty: The Contractor provides a 24-month warranty for the quality of the performed works (installation, connections, programming) from the date of final system commissioning.

- Fault Rectification: During the warranty period, in case of installation or software defects, the Contractor is obliged to fix the problem at its own expense within 24-48 hours of notification.

- Hardware Warranty: Since the Client provides the MICROCOM controllers, the Contractor is not responsible for factory defects of these devices. However, the Contractor is liable for damages caused by incorrect installation or improper electrical connections.

- Software Support: During the warranty period, the Contractor provides software support and, if necessary, makes minor adjustments to the control logic that do not involve fundamental system redesign.