TECHNICAL SPECIFICATIONS

Installation of a Remote Monitoring System for Ultrafiltration (UF) System

1. General Information

Project Name: Implementation of a Remote Monitoring System for Litree WBG6x(N) Series Ultrafiltration Equipment.

Object Description: Samgori Water Treatment Plant, Tbilisi

Client: GWP.

Contractor: _________________________.

2. Project Objective

The objective of this project is to establish continuous, real-time remote monitoring of the Ultrafiltration system's performance. The system shall ensure data acquisition from the local control panel (PLC) and its visualization in the centralized Zeus SCADA system.

Important Note: The system is intended for monitoring purposes only (Read-only). The management process is fully automated by the local control cabinet; therefore, no remote control functionality is required.

3. Existing Control and Transmission Devices

3.1 PLC and Controller Information

Control system:

- PLC System: The ultrafiltration control system is equipped with a Siemens CPU SR40 which is a compact controller from the SIMATIC S7-200 family.

- HMI / Touch Panel: The system is equipped with a Litree touch panel for operator interface and system control.

3.2 Transmission Device

- Controller: A Microcom M103 series controller should be used for data collection and transmission.

- Division of Responsibility:

  - Client: Shall provide the Microcom M103 controller with all necessary modules to the Contractor.

  - Contractor: Shall provide all other necessary auxiliary materials, including but not limited to: mounting enclosures, circuit breakers, internal communication cables and other consumables required for a complete installation.

4. Technical Characteristics and Connectivity

- Internal Communication: Data exchange between the local PLC and the Microcom M103 must be established using Modbus RTU or Modbus TCP protocols.

- Data Transmission: Data transmission from the RTU to the server shall be carried out via GSM (GPRS/LTE) network.

- Software Platform: Visualization shall be implemented in the Zeus SCADA system, ensuring full compatibility with Microcom RTU hardware.

5. Monitoring Parameters (Litree WBG6x(N))

The system must display the following parameters in real-time on the Zeus SCADA monitor:

5.1 Digital and Analog Indicators:

- Electrical energy consumed. (If necessary, add a digital multimeter module with “Fieldbus” communication to the existing system).

- Product Water Turbidity (NTU).

- Water Flow: Instantaneous flow rate (m³/h) and Cumulative flow (Totalizer - m³).

- Pressures: Inlet/Outlet pressure and Transmembrane Pressure (TMP) (Monitoring against the 60 Kpa critical limit).

- Temperature: Product water temperature.

- Levels: Liquid levels (%) in raw water and clean water tanks.

5.2 Statuses and Equipment States:

- Equipment Status: Running/Fault/Stop status for all pumps (Raw water, Backwash, Dosing).

- Valve Positions: Status of all electric valves (Open/Closed).

- Current Cycle: Information on the active process phase (e.g., Production, Backwash, CEB, Standby).

6. Visualization in Zeus SCADA

The visual interface must be intuitive and should closely replicate the HMI screens provided in the Litree equipment manual:

- Process Flow Diagram (P&ID): A visual map of the plant where valves and pumps change color based on their real-time status.

- Trends: Graphical representation of pressure, flow, and turbidity changes over time.

- Event Log: Historical recording of all system messages, alerts, and alarms.

7. Contractor Obligations

- Installation and integration of the Microcom M103 into the existing local control cabinet.

- Configuration of local PLC registers and synchronization with the RTU.

- Setup of GSM connectivity and data mapping within the Zeus SCADA environment.

- Provision of final project documentation (wiring diagrams, Modbus register maps, etc.).

8. Warranty Terms

- Workmanship Warranty: The Contractor provides a 24-month warranty for the quality of the performed works (installation, connections, programming) from the date of final system commissioning.

- Fault Rectification: During the warranty period, in case of installation or software defects, the Contractor is obliged to fix the problem at its own expense within 24-48 hours of notification.

- Hardware Warranty: Since the Client provides the MICROCOM controllers, the Contractor is not responsible for factory defects of these devices. However, the Contractor is liable for damages caused by incorrect installation or improper electrical connections.

- Software Support: During the warranty period, the Contractor provides software support and, if necessary, makes minor adjustments to the control logic that do not involve fundamental system redesign.