Terms of Reference (TOR)

Installation of Control and Monitoring System for Khrami Shaft Wells

1. General Information

Project Name: Installation of a Control and Monitoring System for four distant Shaft Wells at Khrami.

Location: Khrami

Client: GWP

Contractor: _________________________.

2. Project Objective

The objective of the project is to implement a unified, automated control and monitoring system for pump aggregates located at four geographically distant shaft wells. The system shall ensure:

- Maintaining stable water levels in the common collection reservoir.

- Remote control of pumps.

- Visual surveillance of the facilities for security and operational purposes.

3. Description of Current Status

- Currently, management is carried out locally and manually by on-site personnel.

- The reservoir is supplied from a pumping station where pump aggregates are regulated by Variable Frequency Drives (VFD).

- Water supply control is performed manually by personnel at the site.

4. Scope of Work

The Contractor shall provide a complete automation and video monitoring system, including:

- Engineering design and integration of all four wells into a single network.

- Supply and installation of video surveillance systems and other necessary technical equipment.

- Configuration of control software algorithms (Automatic and Manual modes).

- Provision of remote monitoring (Process parameters + Video surveillance).

- Commissioning of the system in fully operational condition.

5. Functional Requirements

5.1 Water Level Measurement

- Shaft Wells: Monitoring of water level (Analog), as well as low-level emergency alarm (Digital).

- Storage Reservoir: Monitoring of water level (Analog), as well as high and low-level emergency alarms (Digital).

5.2 Control Modes and Algorithms The system must provide the following control capabilities:

- Automatic Mode: Start/Stop of pumps based on the water level in the reservoir.

- Remote Manual Mode: Remote manual control (Start/Stop/Reset) from the SCADA interface.

- Local Control: Ability to operate pumps locally at the site.

- Cascade Control: If necessary, sequential starting of pumps to prevent shock loads on the electrical grid.

- Rotation Function: Equal distribution of operating hours among the pumps.

5.3 Monitoring Parameters Visualization shall be implemented in the Zeus SCADA system.

- Reservoir Level: Water level in the storage reservoir (Meters/Percentage).

- Pump Parameters (per aggregate):

  - Power consumption (kW).

  - Current (Amperage).

  - Voltage.

  - Rotation speed (RPM).

  - Pipeline pressure.

  - Emergency statuses and alarm signals.

- Graphs and History: Trends of level changes and a historical Alarm Log.

5.4 Video Monitoring and Security

- To ensure remote control safety, at least one video camera must be installed inside the building of each shaft well.

- The video system shall allow remote personnel to visually assess the situation at the facility without a physical visit.

6. Technical Requirements

6.1 Hardware and Connectivity

- Controller: A Microcom M103 series controller shall be used for data acquisition and transmission.

- Division of Responsibility:

  - Client: Shall provide the Microcom M103 controller with all necessary modules to the Contractor.

  - Contractor: Shall provide control cabinet assembly, video cameras, level sensors, relays, cabling, and all necessary auxiliary materials.

- Communication Protocol: Internal device communication must be established via Modbus RTU/TCP.

- Software Platform: Visualization shall be implemented within the Zeus SCADA system.

6.2 Materials to be Provided by the Contractor The Contractor shall provide the following at its own expense:

- Installation and integration of the video surveillance system.

- Assembly and installation of control cabinets.

- Level sensors, relays, protective elements, and all necessary consumables.

7. Commissioning and Acceptance

- The system is accepted in a fully operational state after testing all modes.

- The Contractor must submit the electrical schematic diagrams of the control cabinets.

8. Warranty Terms

- Workmanship Warranty: The Contractor provides a 24-month warranty for the quality of the performed works (installation, connections, programming) from the date of final system commissioning.

- Fault Rectification: During the warranty period, in case of installation or software defects, the Contractor is obliged to fix the problem at its own expense within 24-48 hours of notification.

- Hardware Warranty: Since the Client provides the MICROCOM controllers, the Contractor is not responsible for factory defects of these devices. However, the Contractor is liable for damages caused by incorrect installation or improper electrical connections.

- Software Support: During the warranty period, the Contractor provides software support and, if necessary, makes minor adjustments to the control logic that do not involve fundamental system redesign.