# Technical Specification for Medium Voltage VFD (630 kW, 6 kV)

## 1. General Requirements

The equipment shall be a medium voltage variable frequency drive (MV VFD) designed for controlling a 630-kW pump-unit, 6 kV induction motor operating at 50 Hz. The VFD must ensure reliable, efficient, and continuous operation under different load conditions.

## 2. Electrical Characteristics

- Motor rated power: 630 kW

- Motor rated voltage: 6 kV

- Input voltage tolerance: –10% ... +10%

- Rated frequency: 50 Hz

- Output voltage range: 0 ... 6 kV

- Output frequency range: 20 ... 50 Hz

- VFD efficiency: ≥98%

## 3. Topology and Construction

- Modular low-voltage power cell design

- Power cell bypass capability (automatic or fast bypass)

- Manual bypass cabinet required (for DOL start)

## 4. Protections

The VFD must include at minimum the following protections:

- Overvoltage/undervoltage

- Overcurrent

- Motor overload

- Phase loss

- Cooling system failure

- Transformer overheating

- Internal communication failure

- IGBT and capacitor protections in each power cell

## 5. Control and Communication

- PID Control with Sleep Mode (Pressure/Flow)

-Communication protocol support: Modbus RTU RS485 (minimum)

- Additional protocols acceptable: Modbus TCP/IP

- HMI: Minimum 10-inch color touchscreen with English interface

## 6. Mechanical and Environmental Requirements

- Installation altitude: Below 1000 m

- Operating temperature: +5 … +40°C

- Cooling method: Forced air cooling

- Enclosure protection: Minimum IP42

- Cable entry: bottom (input and output)

## 7. Additional Components

- One spare power cell module

- One cooling fan unit

- Full air filter set

- Any additional accessories required for safe and continuous operation

## 8. Documentation Requirements

The supplier shall provide:

- Compliance certificates (IEC standards)

- Technical passport

- Electrical schematics

- Installation manual

- Factory Acceptance Test (FAT) reports

## 9. Delivery and Service

- Installation supervision

- Commissioning

- Personnel training

- Minimum warranty period: 24 months