GOGNI WIND FARM
220 kV DOUBLE-CIRCUIT OVERHEAD TRANSMISSION LINE
TECHNICAL SPECIFICATION

| Item | Description |
| --- | --- |
| Project | Gogni Wind Farm 220 kV OHL Gogni 1-2 |
| Country | Georgia |
| Employer / Developer | Gogni Wind Company / AG Energy |
| Transmission System Operator | Georgian State Electrosystem (GSE) |
| Design Engineer | New Power LLC |
| Line Voltage | 220 kV |
| Circuit Arrangement | Double-circuit OHL |
| Route Length | 23.258 km |
| Document Status | Professional technical specification draft |

TABLE OF CONTENTS

1 INTRODUCTION AND APPLICATION	4

1.1 Project-Specific Basis	4

1.2 Definitions	4

2 SCOPE OF WORKS	4

2.1 Main Project Quantities	5

3 APPLICABLE STANDARDS, REGULATIONS AND DESIGN REFERENCES	5

4 DESIGN BASIS AND SERVICE CONDITIONS	6

4.1 Electrical Design Basis	6

4.2 Load Cases for Towers	6

5 ROUTE, PLAN AND PROFILE REQUIREMENTS	7

5.1 Crossings and Congested Corridors	7

6 SURVEY, SETTING OUT AND GEOTECHNICAL VERIFICATION	7

6.1 Geotechnical and Foundation Design Inputs	7

7 TOWERS AND STEEL STRUCTURES	8

7.1 Tower Foot Plates and Anchor Bolt Spacing	8

7.2 Steel Fabrication and Galvanizing	8

7.3 Tower Erection Requirements	8

8 FOUNDATIONS	9

8.1 Excavation and Soil Support	9

8.2 Concrete, Reinforcement and Prefabricated Foundations	9

9 TOWER EARTHING AND LIGHTNING PROTECTION	9

10 CONDUCTORS	10

10.1 Conductor Loads and Tensions	10

10.2 Conductor Accessories	10

11 OPGW, ADSS, FOC AND COMMUNICATION INTERFACE	11

11.1 Optical Fibre Installation Requirements	11

12 INSULATORS, STRINGS, HARDWARE AND LINE ACCESSORIES	11

13 ACCESS ROADS, ROW, ENVIRONMENTAL AND HSE REQUIREMENTS	12

14 CONSTRUCTION METHODOLOGY	12

14.1 Foundation Construction	12

14.2 Tower Assembly and Erection	12

14.3 Conductor and OPGW Stringing	12

14.4 Optical Fibre Works	13

15 INSPECTION AND TEST PLAN	13

15.1 Test Categories	13

16 MINIMUM FACTORY AND MATERIAL TESTS	13

17 MINIMUM SITE TESTS AND CONSTRUCTION ACCEPTANCE	14

18 COMMISSIONING AND ENERGISATION	15

19 DOCUMENTATION AND HANDOVER	15

20 DETAILED TEST MATRIX	16

21 ACCEPTANCE CRITERIA AND NON-CONFORMITIES	17

22 OPEN ITEMS TO BE CONFIRMED	17

23 EMPLOYER PROTECTION, CONTRACTUAL CONTROLS AND REMEDIES	18

23.1 Time for Completion and Critical Milestones	18

23.2 Programme Recovery and Acceleration	18

23.3 Employer Hold Points and Stop-Work Rights	19

23.4 Material Rejection and Replacement Rights	19

23.5 Test Failure, Retesting and Cost Responsibility	19

23.6 Payment Withholding and Set-Off	20

23.7 Quality, HSE and Environmental Breaches	20

23.8 Defects Liability, Warranty and Latent Defects	20

23.9 Contractor Responsibility for Subcontractors and Suppliers	20

23.10 Step-In and Third-Party Rectification Rights	21

23.11 Taking-Over Conditions	21

23.12 Suggested Liquidated Damages and Employer Remedy Schedule	21

24 ENHANCED TECHNICAL COMPLETENESS REQUIREMENTS FOR TENDER ISSUE	21

Appendix A - Project Quantity Summary	23

Appendix B - Contractor Method Statement Requirements	23

Appendix C - Minimum Handover Dossier Index	23

Appendix D - Detailed Technical Requirements by Work Package	25

D.1 Route Survey and Construction Control	25

D.2 Access Roads, Temporary Works and Platforms	25

D.3 Foundation Works	25

D.4 Tower Supply, Storage and Erection	25

D.5 Conductor Stringing	26

D.6 OPGW, ADSS and FOC Works	26

D.7 Crossings and Interface Works	26

D.8 Completion and Reinstatement	27

Appendix E - Detailed Factory Test Requirements	27

Appendix F - Detailed Site Test Procedures and Records	28

F.1 Tower Footing Resistance Measurement	28

F.2 Conductor Sag Measurement	28

F.3 Compression Joint and Dead-End Inspection	28

F.4 Clearance Verification	28

F.5 OPGW/ADSS Optical Testing	29

F.6 Final Line Walkdown	29

Appendix G - Minimum Construction Checklists	29

Annex-1 Gogni OHTL Detailed Project	30

# 1. Introduction and Application

This Technical Specification defines the minimum technical, construction, inspection, testing and commissioning requirements for the 220 kV double-circuit overhead transmission line Gogni 1-2. The line connects the planned 220 kV substation of the Gogni Wind Farm to the 220 kV open switchyard of Kokhra 500 Substation. The document is intended for use in tendering, procurement, construction and acceptance of the overhead line works.

The specification applies to all permanent and temporary works required for the full completion and energisation of the line, including survey, route setting-out, access arrangements, foundations, steel towers, earthing, conductors, OPGW, ADSS/FOC where applicable, insulator strings, hardware fittings, crossings, protection zones, site restoration, tests, as-built documentation and handover.

The Contractor shall execute the Works in accordance with the approved project design, the GSE technical conditions, applicable Georgian legislation, applicable Georgian design norms for 35-750 kV overhead transmission lines, PUE-6 requirements where referenced by the approved design, and applicable IEC/EN standards.

The Contractor shall treat this document as a minimum specification. Where the approved design, GSE requirements, the Environmental and Social Impact Assessment, permit conditions, manufacturer requirements or applicable standards impose more stringent requirements, the more stringent requirement shall apply.

## 1.1 Project-Specific Basis

| Parameter | Project Value |
| --- | --- |
| Project name | 220 kV double-circuit OHL Gogni 1-2 |
| Purpose | Connection of Gogni Wind Farm 220 kV substation to Kokhra 500 substation 220 kV switchyard |
| Installed wind farm capacity used in the design note | 187.2 MW |
| Route municipalities | Tkibuli, Terjola and Zestafoni municipalities |
| Route length | 23.258 km |
| Number of new steel towers | 98 galvanized towers |
| Tower distribution | 77 angle/dead-end towers and 21 suspension/intermediate towers |
| Altitude range along route | 121.3 m to 966.0 m above sea level |
| Right-of-way / protection zone | 25 m from the outermost non-deflected conductor on each side |
| Permanent land use area | 1.5221 ha / 15,221 m² |

## 1.2 Definitions

Employer: The project owner, Gogni Wind Company / AG Energy, or its appointed representative.

Contractor: The entity responsible for executing the OHL works under the Contract.

Engineer: The Employer’s Engineer, Owner’s Engineer or other authorised technical representative.

GSE: Georgian State Electrosystem, the Transmission System Operator.

Approved Design: The working project and drawings prepared by New Power LLC and approved by the Employer/GSE as applicable.

OHL: Overhead transmission line.

OPGW: Optical ground wire installed on the OHL and forming part of the lightning protection and communication system.

ADSS: All-dielectric self-supporting optical fibre cable.

FOC: Underground dielectric fibre optic cable.

HTLS Conductor: High temperature low sag/high-conductivity conductor identified in the project as HTLS conductor-1.

# 2. Scope of Works

The Works shall be performed on a complete and ready-for-operation basis. The scope includes all labour, supervision, engineering, procurement, logistics, plant, equipment, tools, temporary works, testing, documentation and coordination required for successful completion.

• Review of the approved working project, route drawings, plan and profile drawings, tower schedule, foundation schedule and material schedules before construction.

• Detailed survey, check survey, tower location setting-out, verification of existing ground levels and confirmation of statutory clearances.

• Construction access, temporary platforms, vegetation clearing, safety arrangements and site reinstatement.

• Excavation, dewatering where required, foundation installation, backfilling and compaction.

• Supply and erection of galvanized steel towers, including all tower accessories, bolts, nuts, washers, step bolts, anti-climbing devices, danger plates, phase plates and tower identification plates.

• Installation of tower earthing using F12 round steel and associated clamps, bolts, washers and 40x6 mm flat steel where required.

• Installation of HTLS conductor-1 for all six phases of the double-circuit line.

• Installation of OPGW, C-70 shield wire, ADSS and underground FOC as indicated in the approved project.

• Installation of all insulator strings, suspension and tension assemblies, vibration dampers, clamps, connectors, repair sleeves, joint boxes, ODFs and communication accessories.

• Execution of all crossings, clearances and interface works with roads, existing overhead lines, communication lines, pipelines, substations and other utilities.

• Factory, site and commissioning tests, including all required records and acceptance reports.

• Preparation of as-built drawings, test dossiers, operation and maintenance documents and handover files.

## 2.1 Main Project Quantities

| Item | Quantity | Unit / Remark |
| --- | --- | --- |
| OHL route length | 23.258 | km |
| Galvanized steel towers | 98 | pcs / 1,958.479 t |
| HTLS conductor-1 installation | 146.513 | km / 222.700 t |
| OPGW installation | 25.483 | km |
| Underground FOC installation | 0.600 | km |
| ADSS installation between towers No. 60 and No. 61 | 0.327 km design span / 0.400 km procurement length | km |
| C-70 shield wire installation | 1.306 | km |
| Single tension insulator strings for HTLS conductor | 888 | sets |
| Double tension insulator strings for road crossing | 24 | sets |
| Suspension strings for HTLS conductor | 168 | sets |
| OPGW joint boxes | 10 total | 6 OPGW-OPGW, 2 OPGW-ADSS, 2 OPGW-OFC |
| OPGW vibration dampers | 284 | sets |
| HTLS conductor vibration dampers | 1,164 | sets |

# 3. Applicable Standards, Regulations and Design References

The design, materials, construction, testing and acceptance of the OHL shall comply with the latest applicable editions of Georgian legal requirements, GSE technical conditions and the international standards listed below, unless otherwise stated in the approved design.

| Reference | Application |
| --- | --- |
| Georgian framework | GSE technical conditions and connection requirements; Georgian Network Rules; Georgian legislation and permit requirements applicable to transmission line construction. |
| Georgian OHL design norms | Technological design norms for 35-750 kV overhead transmission lines applicable in Georgia. |
| PUE-6 | Electrical Installation Rules, sixth edition, where referenced by the approved design and not conflicting with Georgian legislation. |
| Construction climatology | PN 01.05-08 construction climatology values as applied in the approved design. |
| IEC 60826 | Design criteria of overhead transmission lines. |
| EN 50341 | Overhead electrical lines exceeding AC 1 kV. |
| IEC 61089 | Round wire concentric lay overhead electrical stranded conductors. |
| IEC 61284 | Overhead lines - Requirements and tests for fittings. |
| IEC 60794 series | Optical fibre cables, including OPGW/ADSS/FOC requirements. |
| IEC 60794-4 / IEC 60794-4-10 | Aerial optical cables along electrical power lines / OPGW. |
| IEC 61109 / IEC 60383 / IEC 60437 | Composite and ceramic/glass insulators and RIV/corona tests as applicable. |
| ISO 1461 | Hot dip galvanized coatings on fabricated iron and steel articles. |
| ISO 9001 | Quality management system for manufacturers and contractors. |
| ASTM / EN / ISO material standards | Steel, bolts, concrete materials, galvanizing, testing and measurement standards as applicable. |

The Contractor shall submit a standards compliance matrix before procurement and construction. The matrix shall identify every material, equipment type, construction activity and test with its applicable standard and acceptance criterion.

# 4. Design Basis and Service Conditions

The Contractor shall verify that all materials, installation methods and temporary construction arrangements are suitable for the approved design conditions. No material substitution shall be accepted unless approved by the Employer and demonstrated to be equivalent or superior.

| Design Condition | Value |
| --- | --- |
| Maximum air temperature | +42 °C |
| Minimum air temperature | -27 °C |
| Average annual air temperature | +13.9 °C |
| Temperature during ice condition | -5 °C |
| Temperature during wind condition | -5 °C |
| Temperature during combined wind and ice condition | -5 °C |
| Ice wall thickness | 20 mm, 10-year return period, Region IV |
| Maximum wind speed | 30 m/s, 10-year return period, Region III |
| Route elevation range | 121.3 m to 966.0 m AMSL |
| System frequency | 50 Hz |

## 4.1 Electrical Design Basis

| Item | Requirement |
| --- | --- |
| Nominal voltage | 220 kV |
| Maximum system voltage | 245 kV class where applicable |
| Circuit arrangement | Double circuit, six phases |
| Conductor arrangement | HTLS conductor-1 on both circuits |
| Lightning protection / communication | OPGW 30E39z / OPGW-G652D-2C-127, 24 SMF G.652D |
| Additional shield wire | C-70 in selected spans |
| Special optical crossing | ADSS between towers No. 60 and No. 61 |
| Substation interface | Gogni 220 kV line gantry to Kokhra 500 220 kV line gantry |

## 4.2 Load Cases for Towers

The Contractor shall perform all temporary works, erection and stringing operations in a manner consistent with the tower load assumptions and approved tower checks. The project design considers normal operating and special/emergency loading schemes, including maximum wind, wind plus ice, and broken conductor or shield wire conditions under ice loading.

| Load / Action | Overload / Safety Coefficient |
| --- | --- |
| Self weight of conductor, shield wire, structures and other components | 1.1 / 0.9 where uplift mode applies |
| Ice weight on conductor and shield wire | 2.0 |
| Ice weight on tower structure | 1.3 |
| Wind load on tower structure | 1.2 |
| Wind load on conductor and shield wire without ice | 1.2 |
| Wind load on conductor and shield wire with ice | 1.4 |
| Horizontal conductor/shield wire tension with and without ice | 1.3 / 1.5 where applicable |
| Worker and installation tool loads | 1.3 |

The Contractor shall not apply stringing, pulling or temporary construction loads that exceed the approved tower and foundation design assumptions. For critical angles, steep terrain, long spans and terminal towers, the Contractor shall submit a method statement showing temporary load directions, maximum temporary tensions and hold points.

# 5. Route, Plan and Profile Requirements

The route shall follow the approved plan and profile drawings. The Contractor shall verify the tower locations, tower numbering, route length, elevations, span lengths, crossing points and final clearances before construction.

• The horizontal and vertical scales indicated in the project plan/profile shall be used for verification only; setting-out shall be based on approved coordinates and tower schedule.

• Any discrepancy between drawings, profiles, actual ground levels and existing infrastructure shall be reported immediately to the Engineer.

• Minimum clearances to ground, roads, other overhead lines, structures and utilities shall be checked before stringing and re-checked after final sagging.

• The Contractor shall prepare a crossing method statement for each critical crossing, including outage requirements, scaffolding/guarding arrangements, traffic management and safety distances.

## 5.1 Crossings and Congested Corridors

The approved design indicates that the line route passes through areas congested with existing OHLs and communications. Clearances and approach requirements for compressed conditions shall be maintained in accordance with the approved design and applicable PUE provisions referenced in the project. The span between tower No. 60 and No. 61 crosses the existing 500 kV Imereti OHL; the project applies ADSS in this span due to clearance constraints for OPGW.

The Contractor shall prepare crossing-specific drawings and installation method statements for each road, existing OHL, communication line, pipeline, watercourse and other engineering structure crossing. No crossing work shall start without the Engineer’s approval and any required third-party permission.

# 6. Survey, Setting Out and Geotechnical Verification

The Contractor shall perform a pre-construction check survey including tower centre points, leg positions, terrain levels, access route conditions, visible utilities, environmental constraints and boundary limits.

The Contractor shall verify soil conditions at each tower location before foundation works. Where actual soil differs from the approved geotechnical assumptions, the Contractor shall stop excavation and request instruction from the Engineer.

The Contractor shall prepare survey records for each tower containing coordinates, elevation, tower type, foundation type, leg level differences, adjacent span lengths and noted constraints.

## 6.1 Geotechnical and Foundation Design Inputs

The project identifies several engineering geological elements including clay soils of hard to semi-hard/stiff consistency, sand, gravelly soil with sandy/clayey filler, and limestone bedrock. Foundation selection is based on the engineering-geological conclusion and hydrological references. Groundwater is identified at certain tower locations and shall be managed during excavation and construction.

| Geological Element | General Description |
| --- | --- |
| EGE I | Hard consistency clay soil |
| EGE II | Semi-hard consistency clay soil |
| EGE III | Stiff/plastic clay soil |
| EGE IV | Sand soil |
| EGE V | Gravel/crushed stone soil with sandy and clayey filler |
| EGE VI | Limestone bedrock |

# 7. Towers and Steel Structures

All towers shall be fabricated, galvanized, delivered and erected in accordance with the approved tower drawings, tower schedule, assembly drawings, material lists and this specification. Steel tower material shall be minimum S355 J2 or equivalent unless otherwise indicated in the approved design.

| Tower Type | Quantity | Galvanized Weight |
| --- | --- | --- |
| У220-3 (350) | 2 | 15,500 kg total |
| У220-3+5 (350) | 2 | 20,656 kg total |
| У220-2+5 (350) | 3 | 55,608 kg total |
| У220-2+9 (350) | 22 | 448,118 kg total |
| У220-2+9 (250) | 1 | 20,245 kg total |
| У220-2T+9 (350) | 2 | 41,850 kg total |
| У220-2+14 (350) | 27 | 670,113 kg total |
| У220-2+14 (250) | 3 | 74,085 kg total |
| У220-2T+14 (350) | 2 | 52,028 kg total |
| УС220-6+4 (350) | 2 | 41,318 kg total |
| УС220-6+13 (350) | 4 | 108,420 kg total |
| ПС220-6 (250) | 21 | 184,758 kg total |
| У330-2+9 (350) | 3 | 96,000 kg total |
| 22LA+18-LE3 (350) | 2 | 62,600 kg total |
| 22LA+18+LE0 (350) | 1 | 32,960 kg total |
| 22LA+18+LE3 (350) | 1 | 34,220 kg total |
| Total | 98 | 1,958,479 kg total |

## 7.1 Tower Foot Plates and Anchor Bolt Spacing

The approved design includes tower foot plate configurations with 350 mm or 250 mm anchor bolt spacing. The 350 mm arrangement is used where high mechanical loads require enhanced anchor bolt stability. C939 foot plates of УС220-6 type towers are applied to several tower families as stated in the approved design.

The Contractor shall verify the actual foundation bolt spacing, tower foot plate type and adapter foot requirements before tower delivery. Tower members shall not be modified on site without written approval.

## 7.2 Steel Fabrication and Galvanizing

• Steel sections shall be cut, drilled, punched, bent and fabricated in accordance with approved shop drawings.

• Welded sections shall be inspected according to the approved inspection and test plan. Site welding of galvanized tower components shall not be permitted unless specifically approved.

• All steel tower components, plates, adapter feet, bolts, nuts and washers exposed to weather shall be hot-dip galvanized after fabrication.

• Galvanized surfaces shall be smooth, continuous and free from bare spots, flux deposits, sharp projections, excessive zinc runs and defects affecting installation or service life.

• Touch-up of minor galvanizing defects shall be performed only using approved zinc-rich repair material and procedure. Excessive damage shall be cause for rejection.

## 7.3 Tower Erection Requirements

• Tower erection shall be performed after foundation acceptance and confirmation that concrete strength, anchor bolt alignment and backfilling are acceptable.

• Bolts shall be installed with the specified washers and tightened to the approved torque or tightening procedure.

• Final tower verticality, member alignment, bolt tightening, missing members, redundant members, step bolts, anti-climbing devices and signs shall be checked and recorded.

• The construction sequence shall prevent overstressing of towers. For stability, conductor stringing shall start from the short-span side and then continue to the long span unless the tower operates as a terminal/dead-end support and the approved method statement permits otherwise.

# 8. Foundations

Foundations shall be installed in accordance with the approved foundation drawings and schedules. The design includes prefabricated reinforced-concrete mushroom foundations, reinforced-concrete beams and pile/monolithic reinforced concrete foundations for selected towers.

| Foundation / Component | Quantity |
| --- | --- |
| Ф5-А-350 foundation | 154 pcs / 385 m³ |
| Ф3-А-350 foundation | 32 pcs / 54.4 m³ |
| ФC2-А-350 foundation | 30 pcs / 139.2 m³ |
| ФC1-А-350 foundation | 52 pcs / 219.44 m³ |
| ФC2-4 foundation | 24 pcs / 67.2 m³ |
| Ф5-4 foundation | 84 pcs / 150.36 m³ |
| Ф2.56-4-24 (R) pile foundation | 32 pcs / 104 m³ |
| Adapter foot for foundations | 24 pcs / 5,232 kg |
| P1-A reinforced-concrete beam | 540 pcs / 108 m³ |
| D-12 reinforced-concrete beam fixing details | 1,080 pcs / 5,400 kg |
| D-13 reinforced-concrete beam fixing details | 540 pcs / 5,940 kg |

## 8.1 Excavation and Soil Support

The Contractor shall perform excavation to the approved dimensions and levels. Excavation slopes, shoring, dewatering and worker access shall comply with the approved method statement and HSE plan.

The Contractor shall protect excavations against water accumulation, collapse, contamination and damage. Excavated materials unsuitable for backfill shall be removed or segregated as instructed by the Engineer.

The Contractor shall record the actual soil encountered and the founding level for every tower footing. Photographic records shall be included in the foundation dossier.

## 8.2 Concrete, Reinforcement and Prefabricated Foundations

The project identifies potential chemical aggressiveness of soil leachate against Portland cement concrete and provides for protective measures. Sulphate-resistant concrete or approved protective measures shall be used where required by the approved design. Prefabricated reinforced-concrete foundations and beams shall be coated with hot bitumen twice where specified; anchor bolts, nuts, washers and beam fixing details shall be hot-dip galvanized.

• A 10 cm crushed-stone layer shall be placed below reinforced-concrete foundations where specified to avoid uneven soil deformation.

• Anchor bolts subject to high mechanical loads shall have steel class not less than 8.8 unless the approved design requires higher.

• Concrete placing, compaction, curing and protection shall be controlled in accordance with the approved quality plan.

• Backfilling shall be performed in layers with suitable material and compaction records shall be maintained.

# 9. Tower Earthing and Lightning Protection

Tower earthing shall be executed using F12 round steel and associated connection elements in accordance with the approved tower earthing drawings F-1 and F-2. The line protection system shall comprise OPGW and, in selected spans, C-70 shield wire. Earthing connections shall ensure electrical continuity, corrosion resistance and mechanical robustness.

| Earthing Material | Quantity |
| --- | --- |
| F12 round earthing steel | 7,190 m / 6,471 kg |
| 40x6 mm flat steel, length 160 mm | 63 pcs / 112 kg |
| M16 nuts | 392 pcs |
| M16 bolts | 392 pcs |
| F17 spring washers | 392 pcs |

The Contractor shall measure tower footing resistance at every tower after completion of earthing and before energisation. Corrective measures shall be proposed and implemented if the measured resistance does not meet the approved design or GSE requirements.

The Contractor shall verify metallic continuity between tower body, cross-arms, OPGW/shield wire clamps, earthing down conductors and the buried earthing system.

# 10. Conductors

The phase conductor shall be HTLS conductor-1 as defined in the approved design. The conductor is selected to evacuate the wind farm generation and to allow full export through one circuit in case of outage of the other circuit, considering future expansion and loss reduction objectives.

| HTLS Conductor-1 Characteristic | Project Requirement |
| --- | --- |
| Aluminium material type | A1350-O |
| Nominal aluminium cross-section | ≥470 mm² |
| Nominal core cross-section | ≥56 mm² |
| Nominal calculated total cross-section | ≥526 mm² |
| Calculated conductor diameter | 27 ± 0.8 mm |
| Calculated core diameter | ≤9.6 mm |
| Total nominal weight | ≤1,520 kg/km |
| Aluminium nominal weight | ≤1,410 kg/km |
| Core nominal weight | ≤110 kg/km |
| DC resistance at 20°C | ≤0.0595 ohm/km |
| Core breaking force | ≥121 kN |
| Complete conductor breaking force | ≥148 kN |
| Maximum continuous operating temperature | 180 °C |
| Maximum emergency operating temperature | 200 °C |
| Current carrying capacity at nominal conditions | ≥1,600 A at 180 °C conductor and 40 °C ambient |

## 10.1 Conductor Loads and Tensions

| Parameter | Value |
| --- | --- |
| Self weight load g1 | 1.36 daN/m |
| Ice weight load g2 | 2.61 daN/m |
| Self weight plus ice g3 | 3.97 daN/m |
| Wind load without ice g4 | 1.36 daN/m |
| Wind load with ice at Q=0.25q g5 | 1.31 daN/m |
| Combined self weight and wind without ice g6 | 1.93 daN/m |
| Combined self weight, ice and wind with ice g7 | 4.18 daN/m |
| Permissible tension at maximum temperature | 12.0 daN/mm² |
| Permissible tension at minimum temperature | 12.0 daN/mm² |
| Permissible tension at maximum load wind + ice | 12.0 daN/mm² |
| Mean annual equivalent tension | 7.3 daN/mm² |

## 10.2 Conductor Accessories

| Accessory | Quantity |
| --- | --- |
| Single tension string Type 1 | 828 sets |
| Single tension string Type 4 | 12 sets |
| Single tension string Type 5 | 48 sets |
| Double tension string Type 2 | 24 sets |
| Single suspension string Type 3 | 168 sets |
| Parallel groove clamp PA-HTLS-conductor-1 | 30 pcs |
| Vibration damper VD-4D-HTLS-conductor-1 | 1,164 sets |
| Mid-span joint clamp CC-HTLS-conductor-1 | 48 pcs |
| Repair clamp RC-HTLS-conductor-1 | 36 pcs |

The Contractor shall ensure that all conductor accessories are electrically and mechanically compatible with HTLS conductor-1, including maximum operating temperature, ampacity, mechanical strength, corrosion performance, corona/RIV performance and fatigue resistance.

# 11. OPGW, ADSS, FOC and Communication Interface

The optical communication and lightning protection system shall be installed in accordance with the approved project. OPGW shall be installed from the Gogni 220 kV line gantry to the Kokhra 500 220 kV line gantry. Underground dielectric fibre optic cable shall be installed within the substation areas. ADSS shall be applied in the span between towers No. 60 and No. 61 due to clearance constraints with the existing 500 kV Imereti OHL.

| Item | Specification / Description | Quantity |
| --- | --- | --- |
| OPGW | OPGW-G652D-2C-127 / OPGW 30E39z, 24 SMF G.652D | 25,483 m |
| Underground FOC | Dielectric, rodent resistant, double layer, 24 fibre G.652D | 600 m |
| ADSS | 24 fibre G.652D | 327 m design span / 400 m procurement quantity |
| OPGW single-side non-passing tension set Type 1 | For OPGW | 18 sets |
| OPGW two-side passing tension set Type 2 | For OPGW | 67 sets |
| OPGW suspension set Type 3 | For OPGW | 21 sets |
| OPGW downlead clamps | For towers and line gantries | 450 sets |
| OPGW cable tray / service loop bracket | For towers and gantries | 10 sets |
| OPGW vibration damper 4D-20 or equivalent | Complete with armour rod | 284 sets |
| Joint box OPGW-OPGW | 1xOPGW 24 pcs to 1xOPGW 24 pcs | 6 sets |
| Joint box OPGW-ADSS | 1xOPGW 24 pcs to 1xADSS 24 pcs | 2 sets |
| Joint box OPGW-OFC | 1xOPGW 24 pcs to 1xOFC 24 pcs | 2 sets |
| ODF | GPF01-24ZR with Simplex SC/UPC adapters and 1.5 m G.652D LSZH pigtails | 2 sets |
| ODF panel | Complete set | 1 set |
| Corrugated pipe | 50 mm plastic pipe for fibre optic cable in substation areas | 600 m |

## 11.1 Optical Fibre Installation Requirements

• OPGW and ADSS shall be installed using approved pulling, tensioning and clamping methods that avoid exceeding the manufacturer’s maximum pulling tension, minimum bending radius and crush limits.

• All joint boxes shall be mounted at accessible positions approved by the Engineer and shall include sufficient service loops for future maintenance.

• Splices shall be fusion spliced and protected in splice trays. Splice losses shall comply with the approved acceptance criteria.

• Downlead and service-loop arrangements shall be mechanically secure, UV resistant and protected against abrasion and vandalism.

• ODF/FODP termination shall be labelled fibre-by-fibre and documented in the fibre route and splicing schedule.

# 12. Insulators, Strings, Hardware and Line Accessories

Insulator strings and hardware shall be supplied as complete assemblies suitable for the mechanical loads, creepage requirements, pollution conditions, conductor type, tower type, phase arrangement and approved drawings. All fittings shall comply with IEC 61284 or approved equivalent standards.

The Contractor shall submit complete assembly drawings for each string type, including component references, material grade, rated mechanical strength, dimensions, bolt sizes, tightening torques, cotter pins, locking devices, corona control fittings where applicable and connection details to the tower and conductor.

The Contractor shall supply all insulator strings and hardware with manufacturer type test reports, routine test certificates and factory acceptance test records. Hardware shall be free from sharp edges, cracks, deformation, galvanizing defects and assembly mismatch.

# 13. Access Roads, ROW, Environmental and HSE Requirements

The Contractor shall plan all access and construction activities to minimise environmental, social and land impact. Temporary and permanent land use shall remain within approved boundaries unless additional permits are obtained.

• The 25 m protection zone from the outermost non-deflected conductor on each side shall be respected.

• Vegetation clearing shall be limited to the approved corridor and shall comply with ESIA and permit conditions.

• Topsoil shall be stripped, stored separately and reinstated where required.

• Erosion control shall be provided on slopes, drainage crossings and tower platforms.

• All waste, packaging, fuel and hazardous materials shall be managed under an approved waste and spill prevention plan.

• Work near existing live lines shall be carried out only under an approved electrical safety and outage/permit-to-work procedure.

# 14. Construction Methodology

The Contractor shall submit detailed method statements for every major construction activity. Method statements shall include manpower, equipment, sequence, temporary works, hold points, inspection points, safety risks, environmental measures and acceptance records.

## 14.1 Foundation Construction

• Setting-out and excavation.

• Dewatering and soil support.

• Blinding/crushed-stone layer.

• Anchor bolt/template setting.

• Concrete placement or prefabricated block installation.

• Curing/protection.

• Backfilling/compaction.

• As-built measurements.

## 14.2 Tower Assembly and Erection

• Material receipt inspection.

• Pre-assembly.

• Lifting plan.

• Tower erection.

• Bolt installation/tightening.

• Verticality check.

• Accessories/signage.

• Final inspection.

## 14.3 Conductor and OPGW Stringing

• Drum inspection.

• Pilot wire installation.

• Tension stringing.

• Temporary protection at crossings.

• Jointing/compression.

• Sagging.

• Clipping-in.

• Damper installation.

• Final regulation.

## 14.4 Optical Fibre Works

• Opgw/adss installation.

• Downlead installation.

• Joint box installation.

• Foc trench/duct works.

• Splicing.

• Odf termination.

• Otdr and power-loss tests.

# 15. Inspection and Test Plan

This section defines the minimum test and inspection requirements. The Contractor shall expand this into a project-specific Inspection and Test Plan (ITP), Method Quality Plan (MQP), Field Quality Plan (FQP), Factory Acceptance Test (FAT) procedures and Site Acceptance Test (SAT) procedures before the start of manufacture or construction.

The Contractor shall submit the complete ITP at least four weeks before the relevant activity. The ITP shall define witness points, hold points, acceptance criteria, responsible parties, applicable standards, test equipment and reporting formats.

The Contractor shall provide calibrated test equipment, qualified testing personnel, temporary power, testing facilities, access and all consumables required for inspection and testing. Test equipment calibration certificates shall be valid on the test date.

The Contractor shall issue complete indexed test records in hard copy and editable/searchable electronic format. No material shall be shipped and no work section shall be accepted until all required inspections, tests and non-conformities are closed.

## 15.1 Test Categories

| Test Category | Definition |
| --- | --- |
| Type Tests | Tests proving the design, manufacturing process and general conformity of materials or assemblies. Valid historical type tests may be accepted only if representative of the offered product and approved by the Engineer. |
| Routine Tests | Tests carried out on each unit or production lot as required by the applicable standard and approved ITP. |
| Acceptance / Sample Tests | Tests performed on samples taken from each lot offered for inspection before dispatch or use. |
| Factory Acceptance Tests (FAT) | Witnessed or reviewed tests performed at manufacturer works before dispatch. |
| Site Acceptance Tests (SAT) | Tests performed after installation to demonstrate compliance and readiness for energisation. |
| Commissioning Tests | Final checks and tests required before energisation, including line walkdown, clearance confirmation, phasing, optical link tests and final documentation. |

# 16. Minimum Factory and Material Tests

| Material / Equipment | Minimum Tests and Inspections | Acceptance Criteria |
| --- | --- | --- |
| Steel towers and structures | Material certificates; chemical/mechanical properties; dimensional checks; hole alignment; trial assembly where required; welding/NDT for welded sections; bolt/nut/washer certificates; hot-dip galvanizing thickness, adhesion and appearance; marking and packing inspection. | Steel grade minimum S355 J2 or equivalent; ISO 1461 galvanizing; approved drawings; no missing members, distortion or unacceptable galvanizing defects. |
| Adapter feet and special tower components | Material certificate; dimensional check; fit-up check; galvanizing inspection; trial assembly with anchor bolt pattern where required. | Correct 350 mm or 250 mm interface; compatible with C939 or approved foot plate arrangement; no site modification required. |
| Anchor bolts, nuts, washers | Material grade test certificates; hardness/mechanical tests; thread inspection; galvanizing inspection; dimensional checks. | Anchor bolt class not less than 8.8 where required by project; threads free and fit correctly. |
| Prefabricated reinforced-concrete foundations | Concrete strength certificates; reinforcement certificates; dimensional check; lifting points; embedded parts; visual inspection; protective bitumen coating where required. | Dimensions, concrete grade, reinforcement and coating comply with approved drawings; no cracks, honeycombing or damaged lifting points. |
| Reinforcing steel and concrete materials | Mill certificates; bend/rebend tests where required; cement certificate; aggregate grading; water quality; admixture certificates; mix design approval. | Compliance with approved mix design and relevant standards. |
| HTLS conductor-1 | Dimensional checks; stranding/lay check; DC resistance at 20°C; mass per km; breaking load; stress-strain/creep data; thermal rating evidence; material certificates; surface inspection; drum inspection. | Meets project values including ≥526 mm² total cross-section, 27±0.8 mm diameter, ≤0.0595 ohm/km at 20°C, ≥148 kN breaking force and 180/200°C temperature ratings. |
| Conductor joints and repair sleeves | Dimensional and material checks; mechanical tensile test; electrical resistance test; temperature compatibility check; installation procedure validation. | Compatible with HTLS conductor-1; no excessive resistance or slippage; rated for specified thermal and mechanical duty. |
| Conductor vibration dampers | Dimensional check; clamp slip test; fatigue/performance test evidence; galvanizing/material check; bolt torque verification. | Suitable for span length, conductor diameter and tension; installation distance as manufacturer design. |
| Insulators | Routine mechanical test; visual/dimensional inspection; dry/wet power frequency withstand; lightning impulse/type test evidence; RIV/corona where applicable; marking check. | Rated mechanical strength and electrical withstand consistent with 220 kV service and approved string design. |
| Hardware fittings | Material certificates; dimensional checks; mechanical tensile/slip strength tests; galvanizing test; assembly fit; torque checks. | Complies with IEC 61284 and approved assembly drawings. |
| OPGW | Optical attenuation at 1310/1550 nm; OTDR trace; fibre count and type verification; tensile strength; crush; impact; torsion; temperature cycling; short-circuit/current carrying test evidence; lightning performance evidence; diameter/mass check. | 24 SMF G.652D; mechanically and electrically suitable as optical ground wire; attenuation and splice requirements within approved limits. |
| ADSS | Optical attenuation; tensile/load test evidence; crush/impact; sheath and tracking resistance; span suitability confirmation; drum inspection. | Suitable for tower No. 60-No. 61 span and electrical environment. |
| FOC | Optical attenuation and continuity; sheath integrity; rodent protection verification; dimensional check; drum inspection. | 24 fibre G.652D with double protective layer and rodent resistance as specified. |
| Joint boxes, ODFs and optical accessories | Ingress protection check; fibre tray arrangement; splice protection; adapter/pigtail type; labels; accessories completeness. | Weatherproof, UV-resistant where outdoor, correctly equipped for 24-fibre links. |
| C-70 shield wire | Dimensional check; mass per km; breaking strength; galvanizing; visual inspection; certificates. | Meets project design parameters including 72.58 mm² steel cross-section, 11 mm diameter and 623 kg/km. |

# 17. Minimum Site Tests and Construction Acceptance

| Site Activity / System | Minimum Test / Check | Acceptance Criteria |
| --- | --- | --- |
| Route and setting-out | Verification of tower coordinates, elevations, spans, crossing points, access constraints and foundation positions. | Survey records accepted by Engineer before excavation. |
| Excavation | Check dimensions, depth, founding soil, slope stability, dewatering, and absence of unsuitable material. | Complies with approved foundation drawing and geotechnical assumptions. |
| Concrete works | Slump/consistency, temperature, cube/cylinder strength, placement records, vibration, curing, cover, anchor bolt alignment and level. | Strength and geometry meet design; anchor templates within tolerance. |
| Prefabricated foundation installation | Foundation block integrity, orientation, level, bolt alignment, bitumen coating, backfill and compaction. | No damage; installed to approved position and level. |
| Backfill and compaction | Layer thickness, material suitability, moisture, compaction method and compaction test where specified. | Meets approved compaction requirement; no settlement risk. |
| Tower erection | Member completeness, tower verticality, bolt tightening, missing fasteners, signs, anti-climbing devices, galvanizing damage. | Punch list closed; torque/installation records complete. |
| Tower earthing | Continuity test, buried earth installation inspection, tower footing resistance measurement, connection inspection. | Resistance meets approved requirement/GSE requirement; all bonds continuous. |
| Conductor drums | Drum number, conductor type, drum length, visual damage, certificate check before stringing. | Accepted before pulling. |
| Stringing equipment | Tensioners, pullers, rollers, brakes, pilot wire, communication and grounding arrangements checked. | Equipment certified, suitable and safe. |
| Conductor installation | Tension stringing records; pull tension; anti-twist control; protection at crossings; no conductor ground contact; no bird-caging or damage. | Conductor undamaged and installed within approved tension limits. |
| Jointing and dead-ending | Compression die verification, compression sequence, dimension after compression, identification, location record. | Joint/sleeve dimensions and locations accepted; no joints in prohibited spans unless approved. |
| Sagging and final regulation | Sag measurement under recorded temperature; span-by-span verification; tension records; clipping-in offset. | Sag-tension values within approved stringing chart tolerances. |
| Clearance measurement | Ground clearance, road clearance, existing OHL clearance, pipeline/utility clearance and structure clearance. | All clearances meet approved design and applicable standards. |
| Damper and spacer placement | Location measurement from clamps; quantity per span; clamp torque; visual inspection. | Installed according to approved damper schedule/manufacturer calculation. |
| OPGW/ADSS installation | Sag-tension check, bending radius, downlead clamps, service loops, joint box mounting, earthing bonds where applicable. | No mechanical damage; clearances and loops accepted. |
| Optical pre-installation test | Physical inspection of cable assembly; OTDR continuity and attenuation at 1550 nm; cable length by OTDR. | Results match manufacturer data and approved acceptance limits. |
| Optical post-installation section test | Physical inspection; OTDR continuity, attenuation and length for each installed section. | No abnormal events or excessive attenuation. |
| Optical splice test | Bi-directional OTDR splice loss; splice tray routing; weatherproofing/sealing check. | Splice loss within approved limits; joint box accepted. |
| End-to-end optical commissioning | End-to-end FODP/ODF attenuation at 1310/1550 nm; OTDR trace; fibre identification and labelling. | All fibres continuous, labelled and within link budget. |
| Final line walkdown | Full visual inspection from terminal to terminal, including all towers, signs, hardware, clearances, earthing and reinstatement. | No Category A/B defects; energisation punch list closed. |
| Energisation readiness | Completion of as-built drawings, test dossiers, permits, safety clearances, telecom link tests and GSE/Employer acceptance. | Ready-for-energisation certificate issued. |

# 18. Commissioning and Energisation

Commissioning shall demonstrate that the OHL is mechanically complete, electrically safe, compliant with the approved design and ready for energisation. Energisation shall be performed only after written acceptance by the Employer, GSE and other required authorities.

• Completion of final line patrol and punch list closure.

• Confirmation of phase identification and circuit identification at both terminals.

• Verification of all tower signs, danger plates, phase plates and circuit plates.

• Verification of tower earthing test results and continuity records.

• Verification of final sag, clearances and crossing acceptance records.

• Verification of OPGW/ADSS/FOC end-to-end optical test records and ODF labelling.

• Verification that all temporary earthing, temporary structures and construction materials have been removed.

• Confirmation that protection, communication and SCADA interfaces at substations are ready for line energisation.

• Issue of energisation method statement, switching programme, safety clearances and emergency communication plan.

# 19. Documentation and Handover

The Contractor shall deliver a complete construction and quality dossier. Documents shall be submitted in English unless otherwise agreed, and where Georgian authority submissions are required, Georgian versions shall also be provided.

| Deliverable | Timing |
| --- | --- |
| Project execution plan, WBS and schedule | Before start of works |
| Design review report and standards compliance matrix | Before procurement/construction |
| ITP, MQP, FQP, FAT and SAT procedures | Before manufacturing and site works |
| Material submittals and manufacturer data sheets | Before procurement approval |
| Factory test reports and certificates | Before dispatch |
| Survey and setting-out records | Before excavation / during works |
| Foundation records, concrete tests and as-built measurements | After each foundation batch / tower |
| Tower erection checklists and bolt tightening records | After tower erection |
| Stringing records, sag-tension records and clearance reports | After stringing and final regulation |
| Earthing test reports | After earthing installation |
| OPGW/ADSS/FOC OTDR and optical link test reports | Before energisation |
| Crossing acceptance records and third-party approvals | Before energisation |
| As-built drawings, route GIS/KMZ and tower schedule | Before handover |
| Operation and maintenance manual | Before handover |
| Final quality dossier and completion certificate | At handover |

# 20. Detailed Test Matrix

| Discipline | Test / Check | Description | Frequency | Stage |
| --- | --- | --- | --- | --- |
| Survey | Route control survey | Tower coordinates, elevation, chainage and profile check | All towers | Before excavation |
| Survey | Crossing survey | Existing OHL/road/utility clearance survey | All crossings | Before construction and after stringing |
| Geotechnical | Soil verification | Visual soil classification vs geotechnical design | Each footing | During excavation |
| Geotechnical | Groundwater check | Record water ingress and dewatering requirements | Each excavation | During excavation |
| Concrete | Mix design approval | Cement, aggregate, admixture and water compliance | Each mix | Before concrete works |
| Concrete | Slump/consistency | Workability test | Each truck/batch as per ITP | During concrete placing |
| Concrete | Temperature | Concrete temperature at placing | Each truck/batch as per ITP | During concrete placing |
| Concrete | Compressive strength | Cube/cylinder strength | Each concrete class/batch as per ITP | 7/28 days or as approved |
| Concrete | Cover and reinforcement | Rebar size, spacing, cover, cleanliness | Each cast-in-place foundation | Before pour |
| Concrete | Anchor bolt template | Bolt position, elevation, projection, spacing, plumbness | Each foundation | Before and after pour |
| Foundation | Prefabricated block inspection | Cracks, dimensions, embedded plates, bitumen coating | Each block | Before installation |
| Foundation | Backfill compaction | Layer thickness, material, compaction records | Each foundation | During backfill |
| Steel towers | Material certificate review | Steel grade, bolts, nuts, washers | Each lot | Before fabrication/erection |
| Steel towers | Dimensional inspection | Member dimensions, holes, match marks | Each lot | Factory and site |
| Steel towers | Galvanizing test | Coating thickness and visual quality | Each lot | Factory and site receipt |
| Steel towers | Trial assembly | Fit-up, hole alignment, missing members | Representative tower types | Factory if required |
| Tower erection | Verticality check | Tower plumb and alignment | Each tower | After erection |
| Tower erection | Bolt tightening check | Torque/tightness, lock nuts and washers | Each tower | After erection and before stringing |
| Tower erection | Accessory inspection | Signs, anti-climbing device, step bolts, phase/circuit plates | Each tower | Before commissioning |
| Earthing | Continuity test | Tower body to earthing electrode continuity | Each tower | After earthing |
| Earthing | Footing resistance | Earth resistance measurement | Each tower | After backfill and before energisation |
| Conductor | Drum inspection | Drum ID, length, certificates, visual damage | Each drum | Before stringing |
| Conductor | Conductor certificate review | Diameter, mass, resistance, UTS, thermal rating | Each lot | Before stringing |
| Conductor | Pulling tension record | Maximum pulling and braking tension | Each pull section | During stringing |
| Conductor | Damage inspection | Bird-cage, broken strands, abrasion, contamination | Each section | During and after stringing |
| Conductor | Joint compression check | Die number, compression dimensions, location and marking | Each joint/sleeve | During jointing |
| Conductor | Sag measurement | Sag at recorded temperature vs stringing chart | Each regulated span / section | During final sagging |
| Conductor | Clearance survey | Ground and crossing clearances | All critical spans/crossings | After final regulation |
| Hardware | String assembly inspection | Component orientation, locking devices, cotter pins, torque | Each string | After installation |
| Hardware | Damper inspection | Quantity, location, orientation and clamp torque | Each span | After clipping-in |
| Insulators | Visual inspection | Cracks, chips, contamination, shed condition | Each string | Before and after installation |
| OPGW | Pre-installation OTDR | Continuity, attenuation and cable length | Each drum/segment | Before installation |
| OPGW | Pulling record | Tension, bending radius and sheave diameter | Each pull section | During installation |
| OPGW | Post-installation OTDR | Continuity, attenuation, cable length | Each section | After installation |
| OPGW | Joint box inspection | Sealing, routing, service loops, labels, mounting | Each joint box | After splicing |
| OPGW | Splice loss test | Bi-directional OTDR splice loss | Each splice | After splicing |
| OPGW | End-to-end link test | ODF to ODF attenuation at 1310/1550 nm and OTDR trace | Each fibre | Before commissioning |
| ADSS | Installation inspection | Sag, clamps, bend radius, clearances | Tower 60-61 span | After installation |
| FOC | Duct/trench inspection | Depth, pipe condition, protection and markers | Substation cable routes | During installation |
| FOC | Optical test | Continuity and attenuation | Each fibre | Before handover |
| Crossings | Road crossing check | Clearance and safety/protection measures | Each road crossing | Before and after stringing |
| Crossings | Existing OHL crossing check | Vertical/horizontal clearance and outage/guarding compliance | Each OHL crossing | Before and after stringing |
| Final | Line patrol | Full visual walkdown and punch list | Complete line | Before energisation |
| Final | As-built verification | Tower schedule, coordinates, route, profiles, materials and tests | Complete line | Before handover |
| Final | Energisation readiness review | All documents, permits, tests, GSE/Employer approvals | Complete line | Before energisation |

# 21. Acceptance Criteria and Non-Conformities

A work item shall be accepted only when the relevant approved drawings, specifications, ITP checklists, test procedures and acceptance criteria have been satisfied. Any deviation shall be recorded as a non-conformity and shall be resolved through approved corrective action.

• Material without certificates or with incomplete traceability shall not be installed.

• Conductor, OPGW, ADSS or FOC with visible damage, abnormal OTDR events or unacceptable mechanical damage shall be replaced or repaired only under an approved procedure.

• Tower components with significant galvanizing damage, missing holes, wrong member lengths, non-fitting plates or structural damage shall be rejected.

• Foundations outside tolerance, with inadequate concrete strength, anchor bolt misalignment or insufficient backfill compaction shall not be accepted until corrected.

• Any clearance shortfall after stringing shall be treated as a critical non-conformity and resolved before energisation.

• All non-conformities shall be closed with evidence and Engineer approval before taking-over.

# 22. Open Items to be Confirmed

The following items shall be confirmed during the next revision of this specification or before tender issue:

| Open Item | Responsible Party |
| --- | --- |
| Final GSE technical conditions and connection agreement attachments | Employer / GSE |
| Approved tower schedule with coordinates and foundation type for each tower | Designer / Contractor |
| Final crossing list and third-party permit matrix | Designer / Contractor |
| Final conductor manufacturer datasheet and type test reports | Contractor |
| Final OPGW/ADSS/FOC manufacturer datasheets and link budget | Contractor |
| Final insulator and hardware assembly drawings | Contractor |
| Approved sag-tension charts for all stringing sections | Contractor / Designer |
| Final tower footing resistance acceptance value required by GSE/design | Designer / GSE |
| Outage and protection requirements for crossing existing 500 kV Imereti OHL | GSE / Existing line owner |

# 23. Employer Protection, Contractual Controls and Remedies

This section sets out minimum employer-protection requirements for the 220 kV OHL Works. It is intended to be used together with the Contract Agreement, Particular Conditions, payment schedule and applicable Georgian law. Where this technical specification and the commercial contract differ, the more stringent requirement in favour of safe, timely and compliant completion of the Works shall apply, unless expressly amended by the Employer in writing.

All amounts, percentages and caps in this section shall be confirmed by the Employer and its legal counsel before contract signature. The Contractor shall not rely on the absence of a specific monetary amount in this specification as a limitation of its obligation to complete the Works in accordance with the Contract, approved design, GSE requirements and applicable law.

## 23.1 Time for Completion and Critical Milestones

Time shall be of the essence. The Contractor shall complete the Works, including all tests, energisation-readiness documentation, as-built files and punch-list closure, within the contractual time for completion. The Contractor shall submit a baseline Level-3 schedule and a detailed two-week look-ahead schedule during construction.

• Any delay to approved design review, material approval, tower/foundation manufacturing, foundation completion, tower erection, stringing, OPGW/ADSS/FOC commissioning, GSE/Employer inspections or energisation readiness shall be treated as a critical delay if it affects the completion date or grid connection milestone.

• The Contractor shall immediately notify the Employer of any event that may cause delay and shall submit a recovery plan within three calendar days.

• Approval of a recovery plan shall not waive the Employer’s right to apply liquidated damages or other remedies under the Contract.

| Milestone / Trigger | Minimum Employer Remedy | Suggested Drafting Position |
| --- | --- | --- |
| Delay to contractual completion / ready-for-energisation date | Delay liquidated damages | 0.10% of Contract Price per calendar day, capped at 10% of Contract Price, unless amended in the Contract. |
| Delay to any approved key milestone exceeding 7 days | Milestone LD or payment withholding | 0.05% of Contract Price per day for the affected milestone and withholding of related payment until recovery plan is accepted. |
| Failure to submit acceptable Level-3 schedule, ITP, method statements or material submittals on time | Administrative non-compliance and payment hold | Employer may withhold interim payment for the affected work package until approved documents are submitted. |
| Delay caused by failed tests or rejected materials | Contractor bears all delay consequences | Retesting, replacement, transport, inspection and rework costs to Contractor account; no extension of time unless Employer-caused. |
| Failure to achieve energisation due to Contractor incomplete works/documentation | Completion not achieved | Completion certificate shall not be issued; LD continues until all pre-energisation conditions are met. |

## 23.2 Programme Recovery and Acceleration

If actual progress falls more than 10% behind the approved baseline schedule or any critical activity is delayed by more than seven calendar days, the Employer may require an acceleration and recovery plan. The Contractor shall implement acceleration measures at its own cost where delay is attributable to the Contractor, its subcontractors, vendors or suppliers.

• Acceleration may include additional crews, extended shifts, additional stringing equipment, alternative logistics, additional testing resources and parallel work fronts.

• The Contractor shall not compromise HSE, quality, clearances, tower loading limits, conductor handling requirements or optical fibre handling requirements to recover time.

• Failure to implement an accepted recovery plan shall constitute a material breach of contract.

## 23.3 Employer Hold Points and Stop-Work Rights

The Employer and Engineer shall have the right to establish hold points and witness points for any activity affecting safety, quality, permanent works performance, future operation or GSE acceptance. Work beyond a hold point without written release shall be treated as unauthorised work and may be rejected.

| Hold Point | Work Cannot Proceed Until | Minimum Evidence Required |
| --- | --- | --- |
| Material manufacture release | Material submittals and ITP accepted | Approved drawings, datasheets, certificates, FAT procedure. |
| Dispatch from factory | FAT / inspection release issued | Signed inspection release note and complete shipment dossier. |
| Foundation concrete / precast placement | Excavation and founding soil accepted | Survey records, geotechnical confirmation, template check. |
| Tower erection | Foundation accepted | Concrete strength/precast acceptance, bolt alignment, backfill records. |
| Stringing | Tower erection accepted | Verticality, bolt tightening, earthing readiness, crossing permits. |
| Crossing of existing OHL/road/utility | Crossing method accepted | Permit/outage/guarding plan and safety approval. |
| Energisation | All SAT and documentation accepted | Clearance report, earthing report, optical tests, punch-list closure, GSE/Employer approval. |

The Employer may suspend any work that is unsafe, non-compliant, undocumented, outside the approved method statement, environmentally damaging, or likely to cause future operational risk. Suspension due to Contractor default shall not entitle the Contractor to additional time or cost.

## 23.4 Material Rejection and Replacement Rights

The Employer may reject any material, equipment or work that does not comply with this specification, the approved design, GSE requirements, approved manufacturer data, applicable standards or good utility practice. Rejected items shall be removed from site and replaced at the Contractor’s cost.

• Material without traceable certificates, test reports and approved manufacturer data shall not be installed.

• Steel tower components with wrong dimensions, wrong hole patterns, distorted members, missing members, unacceptable galvanizing damage or insufficient marking shall be rejected.

• HTLS conductor, OPGW, ADSS or FOC with bird-caging, broken strands, kinks, crushing, sheath damage, abnormal OTDR events or uncontrolled bending shall be replaced unless an approved repair procedure is accepted by the Engineer.

• Foundations with unacceptable concrete strength, incorrect founding level, anchor bolt misalignment, inadequate compaction or non-conforming protective coating shall not be accepted until corrected.

## 23.5 Test Failure, Retesting and Cost Responsibility

All testing costs, including repeated tests required due to Contractor failure, material non-compliance, incorrect installation or incomplete documentation, shall be borne by the Contractor. The Contractor shall also bear the cost of Employer/Engineer travel, third-party inspection, laboratory testing and GSE re-inspection arising from failed or repeated tests, unless the failure is solely caused by the Employer.

| Failure Event | Contractor Obligation | Employer Right |
| --- | --- | --- |
| Factory test failure | Rectify, replace or redesign and repeat FAT | Reject shipment and suspend payment for affected lot. |
| Site test failure | Correct installation and repeat SAT | Refuse acceptance of affected section. |
| OPGW/ADSS/FOC OTDR failure or excessive attenuation | Locate fault, repair/replace cable or splice, retest end-to-end | Require replacement of complete cable section if reliability is affected. |
| Tower footing resistance above limit | Install approved additional earthing and retest | Withhold tower/section acceptance. |
| Clearance shortfall | Correct sag, tower works or other approved measure | Prohibit energisation until resolved. |
| Repeated non-conformity | Root-cause analysis and corrective action plan | Require removal of subcontractor/vendor or enhanced inspection at Contractor cost. |

## 23.6 Payment Withholding and Set-Off

The Employer may withhold payment or set off amounts from interim payments, retention, performance security or final payment where the Contractor fails to meet contractual requirements. Payment withholding shall not be considered acceptance of defective or incomplete work.

• Payment may be withheld for missing quality records, incomplete as-built drawings, unresolved NCRs, failed tests, outstanding HSE/environmental issues, unapproved substitutions or incomplete handover dossiers.

• No payment shall be due for materials delivered to site but not accepted, materials without certificates, or works executed without required hold-point release.

• The Employer may deduct the cost of third-party rectification where the Contractor fails to correct defects within the instructed period.

## 23.7 Quality, HSE and Environmental Breaches

The Contractor shall be fully responsible for quality, health and safety, environmental management, landowner interface and compliance with permits. The Employer’s approval or inspection shall not relieve the Contractor of these obligations.

| Breach | Minimum Consequence | Additional Employer Right |
| --- | --- | --- |
| Work without approved method statement / permit to work | Immediate stop-work instruction | Removal of responsible personnel from site. |
| Serious HSE breach or near miss | Work suspension and corrective action plan | Replacement of site manager/HSE manager if repeated. |
| Environmental damage, spill, illegal dumping or unauthorised tree cutting | Immediate remediation at Contractor cost | Back-charge, reporting to authorities and suspension. |
| Damage to road, land, fence, crop, utility or third-party asset | Repair/compensation at Contractor cost | Withhold payment until settlement evidence. |
| Repeated quality non-conformities | Enhanced inspection regime | All additional inspection cost to Contractor. |

## 23.8 Defects Liability, Warranty and Latent Defects

The Contractor shall warrant that the Works are free from defects in design portions performed by the Contractor, materials, workmanship, installation and testing. Unless a longer period is stated in the Contract, the defects liability period shall not be less than 24 months from taking-over or 24 months from energisation, whichever is later. Latent defects affecting safety, structural integrity, electrical performance or optical communication reliability shall remain the Contractor’s responsibility in accordance with the Contract and applicable law.

• During the defects liability period, the Contractor shall respond to emergency defects within 24 hours and mobilise corrective action within 72 hours, unless a shorter period is required for safety or grid security.

• Repaired or replaced components shall carry a renewed defects liability period for the repaired/replaced item.

• The Contractor shall provide spare parts, special tools and technical support necessary to maintain the line during the defects liability period.

## 23.9 Contractor Responsibility for Subcontractors and Suppliers

The Contractor shall remain fully responsible for all subcontractors, manufacturers, vendors, laboratories, transporters and service providers. Approval of a subcontractor or manufacturer by the Employer shall not create any contractual relationship between the Employer and such party and shall not relieve the Contractor of responsibility.

• The Employer may require replacement of any subcontractor or vendor that repeatedly fails to meet quality, safety, schedule or documentation requirements.

• All manufacturer warranties, test reports, software/native OTDR files, as-built drawings and technical data shall be transferred to the Employer without restriction.

## 23.10 Step-In and Third-Party Rectification Rights

If the Contractor fails to correct a critical defect, safety issue, environmental damage, delay or non-conformity within the instructed period, the Employer may perform the work itself or engage a third party to perform the work. All related costs, including management, inspection, testing, mobilisation and delay consequences, may be deducted from amounts due to the Contractor or recovered under the Contract.

## 23.11 Taking-Over Conditions

The line shall not be taken over and completion shall not be certified until all conditions below are satisfied. Partial energisation, if any, shall not constitute taking-over unless expressly certified in writing by the Employer.

• All permanent works are complete, tested and accepted.

• All critical and major punch-list items are closed.

• GSE and other required authority approvals for energisation are obtained.

• Final route clearance, crossing clearance, tower earthing, OPGW/ADSS/FOC optical tests and sag-tension records are accepted.

• As-built drawings, GIS/KMZ files, tower schedule, material reconciliation, test dossiers and O&M documents are submitted and accepted.

• All land, access, reinstatement, waste, damage and environmental obligations are closed or secured to the Employer’s satisfaction.

## 23.12 Suggested Liquidated Damages and Employer Remedy Schedule

The following table is a recommended employer-protection schedule to be reviewed by the Employer’s legal counsel and incorporated into the Contract Particular Conditions or Special Conditions. These provisions are intended to give the Employer practical leverage without replacing the legal contract.

| No. | Issue | Suggested Remedy / LD |
| --- | --- | --- |
| 1 | Delay to completion / energisation readiness | 0.10% of Contract Price per calendar day, capped at 10%. |
| 2 | Delay to approved critical milestone | 0.05% of Contract Price per calendar day for the affected milestone; recoverable until milestone recovery. |
| 3 | Failure to submit accepted as-built and handover dossier | Withhold minimum 5% of Contract Price or final payment until accepted. |
| 4 | Repeated failed FAT/SAT caused by Contractor | All retesting and inspection costs plus schedule consequences to Contractor. |
| 5 | Unauthorised material substitution | Reject material; replacement at Contractor cost; no time extension. |
| 6 | Unapproved work beyond hold point | Employer may require exposure, dismantling, retesting or reconstruction at Contractor cost. |
| 7 | HSE/environmental serious breach | Stop work; corrective action; back-charge; potential removal of personnel. |
| 8 | Damage to third-party utilities or land | Contractor indemnifies Employer and bears repair/compensation cost. |
| 9 | Failure to correct defects during defects liability period | Employer step-in/right to recover costs; warranty extension for repaired item. |
| 10 | Non-compliant clearance preventing energisation | Critical defect; no taking-over; LD continues until corrected and approved. |

# 24. Enhanced Technical Completeness Requirements for Tender Issue

For tender issue and contractual enforceability, this specification should not remain limited to a high-level technical draft. The Contractor shall be provided with, and shall be bound by, a complete tender package including approved design drawings, schedules, BOQ, interface matrices, permit requirements, inspection and test plans and acceptance criteria. The following requirements shall be completed before final tender release.

| Required Tender Attachment | Purpose | Status / Action |
| --- | --- | --- |
| Approved OHL route plan and profile | Controls route, spans, elevations and clearances | Attach latest approved drawing set. |
| Tower schedule / spotting list | Controls tower type, coordinates, deviation angle, span and foundation type | Attach final approved schedule. |
| Foundation schedule and drawings | Controls excavation, foundation, anchor bolt and adapter foot requirements | Attach final approved drawings. |
| Conductor/OPGW/ADSS/FOC datasheets | Controls procurement and testing acceptance | Require manufacturer submittals and type tests. |
| Sag-tension charts | Controls stringing, final sag and clearance verification | Make final charts a contractual deliverable before stringing. |
| Crossing register and permit matrix | Controls third-party interface and construction permits | Attach road/OHL/pipeline/utility crossings. |
| Detailed ITP and test forms | Controls inspection, hold points and acceptance | Contractor to develop; Employer to approve before works. |
| Employer remedy and LD schedule | Protects Employer against delay, non-compliance and incomplete handover | Legal review and insert into Contract conditions. |

A 24-page document is sufficient only as a preliminary technical framework. For an Employer-side tender and construction contract, the final OHL specification should normally be expanded to include detailed materials requirements, construction procedures, testing procedures, acceptance forms, contractual hold points, documentation requirements and employer remedies. This updated version therefore adds a dedicated employer-protection section and should be further expanded with the final project attachments listed above.

# Appendix A - Project Quantity Summary

The following summary has been prepared from the approved working project quantities and shall be used as a technical reference. The Contractor shall verify all quantities against the latest approved BOQ and drawings before procurement.

| Category | Summary |
| --- | --- |
| Foundations and beams | See Section 8. Includes Ф5-А-350, Ф3-А-350, ФC2-А-350, ФC1-А-350, ФC2-4, Ф5-4, Ф2.56-4-24 (R), P1-A beams and D-12/D-13 fixing details. |
| Towers | 98 hot-dip galvanized steel towers with total weight 1,958.479 t. |
| Conductor | HTLS conductor-1, 146.513 km, 222.700 t. |
| OPGW | 25.483 km OPGW-G652D-2C-127 / 24 SMF G.652D. |
| FOC | 600 m underground dielectric rodent-resistant double-layer fibre cable. |
| ADSS | 327 m design span between towers 60-61; procurement quantity 400 m. |
| C-70 shield wire | 1.306 km. |
| Earthing | F12 round steel 7,190 m / 6,471 kg. |

# Appendix B - Contractor Method Statement Requirements

| Method Statement | Minimum Content |
| --- | --- |
| Survey and setting-out method statement | Coordinate system, equipment calibration, control points, setting-out tolerance, tower centre and leg position marking, protection of survey marks. |
| Access and traffic method statement | Access route, road improvements, temporary bridges/culverts, traffic control, restoration. |
| Excavation and foundation method statement | Excavation sequence, shoring, dewatering, soil disposal, concrete or prefabricated foundation installation, backfill. |
| Tower erection method statement | Assembly area, lifting equipment, rigging, crane calculations, exclusion zones, bolt tightening, work-at-height controls. |
| Stringing method statement | Pulling sections, tension limits, crossing protection, rollers, pilot rope, communication, emergency release, temporary earthing. |
| OPGW/ADSS/FOC method statement | Cable handling, drum storage, pulling tensions, bend radius, jointing, service loops, OTDR testing and labelling. |
| Crossing method statement | Crossing drawings, temporary protection, outages, safety distances, third-party approvals, clearance verification. |
| Testing and commissioning method statement | SAT procedures, test equipment, acceptance criteria, reporting, energisation readiness. |

# Appendix C - Minimum Handover Dossier Index

| Volume | Dossier Content |
| --- | --- |
| 01 | Approved drawings, design calculations and revisions |
| 02 | Permits, GSE approvals and third-party crossing approvals |
| 03 | Material certificates and manufacturer test reports |
| 04 | Factory inspection and FAT reports |
| 05 | Survey and setting-out records |
| 06 | Foundation dossiers by tower |
| 07 | Tower erection dossiers by tower |
| 08 | Conductor and OPGW stringing records |
| 09 | Sag-tension and clearance reports |
| 10 | Earthing test reports |
| 11 | Optical fibre OTDR and link-loss reports |
| 12 | Non-conformity reports and corrective actions |
| 13 | Final line patrol records and punch list closure |
| 14 | As-built drawings, route GIS/KMZ, tower schedule and material reconciliation |
| 15 | Operation and maintenance manual and recommended spare parts list |

# Appendix D - Detailed Technical Requirements by Work Package

This appendix expands the minimum requirements into work-package level technical clauses. It shall be read together with the main body of the specification, the approved working project, plan and profile drawings, tower and foundation schedules, BOQ and all GSE requirements.

## D.1 Route Survey and Construction Control

The Contractor shall the Contractor shall establish permanent and temporary benchmarks referenced to the approved project coordinate and elevation system. Benchmarks shall be protected throughout the construction period and included in the as-built survey file.

The Contractor shall Before tower excavation, the Contractor shall re-check each tower centre, leg position, diagonal direction, local ground slope, access constraints and potential conflict with underground or overhead utilities. Any discrepancy shall be recorded in a Survey Query Register and submitted for instruction.

The Contractor shall the Contractor shall prepare a tower-by-tower survey sheet showing tower number, tower type, station/chainage, ground elevation, leg elevations, adjacent span lengths, deviation angle, crossing references and required foundation type.

The Contractor shall After erection and stringing, the Contractor shall carry out final profile and clearance surveys for all critical spans. Results shall be compared against the approved plan/profile and applicable minimum clearance requirements.

## D.2 Access Roads, Temporary Works and Platforms

The Contractor shall Access tracks, crane pads, stringing pads, drum sites and pulling/tensioning locations shall be selected to avoid unnecessary land disturbance and shall be approved by the Engineer before use.

The Contractor shall Temporary works shall be designed for the actual equipment loads, soil conditions, slopes, drainage and weather conditions. Temporary works shall not compromise existing roads, structures, drainage lines or environmental features.

The Contractor shall Access road construction shall include drainage, erosion protection and reinstatement requirements. Any damage to public/private roads, agricultural land, fences or utilities caused by the Contractor shall be repaired at the Contractor’s cost.

The Contractor shall Tower platforms shall be graded only to the minimum extent required for safe construction. Topsoil and subsoil shall be stored separately where required and reinstated after completion.

## D.3 Foundation Works

The Contractor shall Foundation excavation shall proceed only after survey acceptance, utility check, permit-to-dig approval and HSE controls are in place. Excavation limits shall be marked and guarded.

The Contractor shall Foundation bottom shall be inspected by the Engineer before placing blinding, crushed stone layer or prefabricated elements. Soft spots, unsuitable material or water-bearing zones shall be reported and treated only under approved instruction.

The Contractor shall For cast-in-place or pile foundations, reinforcement shall be clean, correctly placed, securely tied and supported to maintain specified cover. Anchor bolt cages and templates shall be fixed against movement during concrete placement.

The Contractor shall Concrete shall not be placed in standing water, contaminated excavation or unsuitable weather conditions unless an approved procedure is in place. Concrete shall be compacted without segregation and cured against rapid drying, freezing, rain and contamination.

The Contractor shall Backfilling shall not start until the Engineer accepts the foundation installation. Backfill material shall be placed in layers, compacted and shaped to shed water away from the tower legs. Rock or debris that may damage coatings or buried earthing shall not be used adjacent to structural components.

## D.4 Tower Supply, Storage and Erection

The Contractor shall Tower components shall be delivered with packing lists and markings enabling tower-by-tower traceability. Components shall be stored on timber or suitable supports above ground to avoid corrosion, deformation or loss of small parts.

The Contractor shall Galvanized members shall be handled with slings or lifting devices that do not damage the coating. Dragging members directly on soil or rock is prohibited.

The Contractor shall Tower erection shall follow the approved erection drawings and sequence. Temporary bracing, guys or supports shall be used where required by the erection method statement.

The Contractor shall Bolts shall be installed in the correct direction and with the correct washer/nut arrangement. Bolt tightening shall be performed progressively and re-checked after tower completion and before stringing.

The Contractor shall After tower completion, missing members, distorted members, open holes, poor alignment, sharp edges, damaged galvanizing and loose bolts shall be recorded and corrected before stringing works.

## D.5 Conductor Stringing

The Contractor shall Tension stringing shall be the preferred method for HTLS conductor installation. Manual stringing shall be used only where approved and only with measures preventing conductor damage and uncontrolled sag.

The Contractor shall Drum handling shall prevent contamination, nicking, kinking, flattening or bird-caging. Conductors shall not be dragged on the ground, tower steel, rocks, roads, vegetation or temporary structures.

The Contractor shall Rollers and sheaves shall be suitable for the conductor diameter and minimum bending radius. Sheaves shall be clean, aligned and free-running before pulling.

The Contractor shall Pulling tension and sagging tension shall be recorded continuously or at intervals approved by the Engineer. Pulling shall stop immediately if abnormal tension, vibration, snagging, loss of communication or unsafe condition occurs.

The Contractor shall Compression joints, dead-ends and repair sleeves shall be installed only by trained personnel using manufacturer-approved tools, dies and procedures. Every compression shall be identified, measured and recorded.

## D.6 OPGW, ADSS and FOC Works

The Contractor shall OPGW shall be handled as both an electrical shield wire and an optical communication cable. Mechanical damage, excessive tension, over-bending, crushing or torsion shall not be permitted.

The Contractor shall OPGW and ADSS pulling equipment shall include tension monitoring. The Contractor shall maintain bend radius, sheave diameter and pulling tension within manufacturer limits.

The Contractor shall Joint boxes shall be mounted in positions that allow safe future access without compromising electrical clearances. Downlead clamps shall be spaced in accordance with the approved design/manufacturer recommendations.

The Contractor shall Optical fibre splicing shall be performed in clean, controlled conditions using calibrated fusion splicing equipment. Every fibre shall be labelled, mapped and tested.

The Contractor shall Underground FOC shall be installed in approved protective pipe/duct, with route markers and mechanical protection where required. Bending radius and pulling tension shall comply with manufacturer requirements.

## D.7 Crossings and Interface Works

The Contractor shall For each crossing, the Contractor shall prepare a crossing sheet showing crossing type, chainage, adjacent towers, span length, existing asset owner, required permit/outage, temporary protection, minimum clearance and acceptance measurement method.

The Contractor shall Works near live overhead lines shall be carried out under an approved electrical safety plan. Induced voltage hazards shall be assessed and controlled through temporary earthing and bonding.

The Contractor shall Road crossings shall include traffic management, warning signs, guards, communication between pulling points and emergency stop arrangements.

The Contractor shall Crossings of pipelines, communications, rivers or sensitive infrastructure shall not proceed until the relevant owner/authority has approved the method statement where required.

## D.8 Completion and Reinstatement

The Contractor shall After completion of each tower site, the Contractor shall remove temporary materials, waste, surplus excavation material and construction debris. The area shall be reinstated to the approved condition.

The Contractor shall Drainage shall be restored and erosion controls shall remain in place until vegetation or final stabilisation is effective.

The Contractor shall All access tracks not required for permanent access shall be reinstated unless otherwise instructed by the Employer or landowner.

# Appendix E - Detailed Factory Test Requirements

Factory tests shall be performed at the manufacturer’s works or approved test laboratories before dispatch. The Contractor shall submit test procedures, sampling plans, calibration certificates and acceptance criteria for approval. The following tables state minimum requirements and shall not limit the requirements of applicable standards.

| Item | Factory Test / Inspection | Description | Acceptance Basis |
| --- | --- | --- | --- |
| Tower steel and galvanized members | Steel grade verification | Review mill certificates; perform sample tensile, yield, elongation and chemical analysis tests where required. | Approved standard / approved design / manufacturer procedure |
| Tower steel and galvanized members | Dimensional inspection | Check length, hole diameter, pitch, edge distance, bends, end cuts, markings and matching against approved shop drawings. | Approved standard / approved design / manufacturer procedure |
| Tower steel and galvanized members | Fit-up / trial assembly | Assemble representative tower body, cross-arm, peak and special/adapted foot sections to prove hole alignment and constructability. | Approved standard / approved design / manufacturer procedure |
| Tower steel and galvanized members | Hot-dip galvanizing test | Measure zinc coating thickness, adhesion and uniformity; inspect for bare spots, ash, flux deposits, spikes and runs. | Approved standard / approved design / manufacturer procedure |
| Tower steel and galvanized members | Packing inspection | Verify packing lists, bundle numbers, tower number allocation and protection against transportation damage. | Approved standard / approved design / manufacturer procedure |
| Fasteners and anchor bolts | Mechanical tests | Verify property class, tensile strength, proof load and hardness as applicable. | Approved standard / approved design / manufacturer procedure |
| Fasteners and anchor bolts | Thread and fit check | Check thread quality, nut run, washers and compatibility with tower holes/anchor templates. | Approved standard / approved design / manufacturer procedure |
| Fasteners and anchor bolts | Galvanizing check | Verify coating thickness and no thread seizure after galvanizing. | Approved standard / approved design / manufacturer procedure |
| HTLS conductor-1 | Conductor construction | Verify strand numbers, strand diameters, lay direction, overall diameter and surface condition. | Approved standard / approved design / manufacturer procedure |
| HTLS conductor-1 | Electrical resistance | Measure DC resistance at 20°C and correct measured values to reference temperature. | Approved standard / approved design / manufacturer procedure |
| HTLS conductor-1 | Mechanical strength | Verify ultimate tensile strength of complete conductor and core; review stress-strain and creep curves. | Approved standard / approved design / manufacturer procedure |
| HTLS conductor-1 | Thermal performance | Review type test evidence for 180°C continuous and 200°C emergency operation and ampacity of at least 1600 A under project conditions. | Approved standard / approved design / manufacturer procedure |
| HTLS conductor-1 | Drum inspection | Verify drum length, drum identification, packing, certificates and absence of shipping damage. | Approved standard / approved design / manufacturer procedure |
| Insulators and fittings | Mechanical strength | Perform sample tensile/mechanical load tests on strings and critical hardware components. | Approved standard / approved design / manufacturer procedure |
| Insulators and fittings | Electrical withstand | Review dry/wet power frequency and lightning impulse test reports for the insulator type. | Approved standard / approved design / manufacturer procedure |
| Insulators and fittings | Assembly check | Verify every string component, locking pin, yoke plate, shackle, clamp and corona fitting against approved assembly drawings. | Approved standard / approved design / manufacturer procedure |
| Insulators and fittings | Galvanizing and material | Check coating thickness, surface finish and material certificates. | Approved standard / approved design / manufacturer procedure |
| OPGW / ADSS / FOC | Optical tests | Measure attenuation at 1310 nm and 1550 nm, continuity and length using OTDR for each drum. | Approved standard / approved design / manufacturer procedure |
| OPGW / ADSS / FOC | Mechanical tests | Review tensile, crush, impact, torsion and vibration test evidence as applicable. | Approved standard / approved design / manufacturer procedure |
| OPGW / ADSS / FOC | Electrical/thermal tests for OPGW | Review short-circuit current carrying, lightning and temperature cycling type test evidence. | Approved standard / approved design / manufacturer procedure |
| OPGW / ADSS / FOC | Fibre verification | Verify 24 SMF G.652D fibre count, colour code and manufacturer certificates. | Approved standard / approved design / manufacturer procedure |
| OPGW / ADSS / FOC | Accessory inspection | Check joint boxes, ODFs, downlead clamps, service-loop brackets and dampers for completeness and compatibility. | Approved standard / approved design / manufacturer procedure |
| C-70 shield wire | Dimensional and mass checks | Verify diameter, steel cross-section and mass per km. | Approved standard / approved design / manufacturer procedure |
| C-70 shield wire | Mechanical strength | Verify breaking strength and strand integrity. | Approved standard / approved design / manufacturer procedure |
| C-70 shield wire | Galvanizing | Check zinc coating and surface condition. | Approved standard / approved design / manufacturer procedure |
| Concrete and precast elements | Factory/precast concrete certificates | Verify concrete strength, reinforcement, dimensions, lifting anchors and protective coating. | Approved standard / approved design / manufacturer procedure |
| Concrete and precast elements | Bitumen/protective coating | Check coating coverage and thickness where specified. | Approved standard / approved design / manufacturer procedure |
| Concrete and precast elements | Embedded steel | Verify anchor details, galvanized components and dimensions. | Approved standard / approved design / manufacturer procedure |

# Appendix F - Detailed Site Test Procedures and Records

The Contractor shall prepare step-by-step site test procedures. Each procedure shall identify safety precautions, equipment, calibration, environmental limits, personnel qualifications, test sequence, readings to be recorded and acceptance criteria. The following sub-sections define minimum procedure content.

## F.1 Tower Footing Resistance Measurement

• Use a calibrated earth resistance tester and an approved fall-of-potential or clamp method suitable for the site conditions.

• Disconnect parallel paths where required by the test method or record the test configuration if disconnection is not possible.

• Record tower number, tower type, weather, soil condition, test method, electrode spacing, measured resistance and corrective actions.

• If the result exceeds the approved design/GSE limit, install additional counterpoise/earth electrodes or other approved measures and retest.

## F.2 Conductor Sag Measurement

• Measure conductor temperature at the time of sagging using an approved thermometer or conductor temperature method.

• Use the approved sag-tension chart for the exact ruling span, conductor temperature and stringing section.

• Record target sag, measured sag, ambient temperature, conductor temperature, span reference and final adjustment.

• Repeat sag checks after clipping-in and after any significant change affecting tension.

## F.3 Compression Joint and Dead-End Inspection

• Verify conductor cleaning, inhibitor compound, insertion length, die size, compression sequence and number of compressions before work starts.

• Measure compressed dimensions and compare with manufacturer requirements.

• Mark every joint/dead-end with unique ID and record tower/span location, installer, tool/die number and inspection result.

• Joints shall not be located in prohibited crossing spans unless specifically approved.

## F.4 Clearance Verification

• Perform clearance survey after final sagging and before energisation.

• For roads, existing OHLs and utilities, record vertical and horizontal clearance under the appropriate design temperature/loading condition or apply approved correction.

• Prepare a clearance report with sketches, photographs and survey points for every critical crossing.

• Any clearance below requirement shall be corrected before energisation.

## F.5 OPGW/ADSS Optical Testing

• Perform OTDR testing before installation, after installation, after splicing and end-to-end from ODF to ODF.

• Test at both 1310 nm and 1550 nm unless otherwise approved. Bi-directional results shall be used for splice loss evaluation.

• Record fibre number, wavelength, test direction, launch/receive fibre, attenuation, length, event table and trace file.

• All traces shall be submitted in native electronic format and PDF summary.

## F.6 Final Line Walkdown

• Walk or inspect the complete line from gantry to gantry.

• Check tower numbers, phase plates, circuit plates, danger signs, anti-climbing devices, hardware, dampers, earthing, OPGW/ADSS downleads, clearances and reinstatement.

• Classify defects as critical, major or minor. Critical and major defects shall be closed before energisation.

• Submit signed walkdown sheets with photographs for every tower and crossing.

# Appendix G - Minimum Construction Checklists

| Checklist | Item | Result | Remarks |
| --- | --- | --- | --- |
| Foundation checklist | Survey accepted | Accept / Reject / N/A | Remarks / reference to record |
| Foundation checklist | Excavation dimensions checked | Accept / Reject / N/A | Remarks / reference to record |
| Foundation checklist | Founding soil accepted | Accept / Reject / N/A | Remarks / reference to record |
| Foundation checklist | Dewatering completed | Accept / Reject / N/A | Remarks / reference to record |
| Foundation checklist | Crushed-stone/blinding layer accepted | Accept / Reject / N/A | Remarks / reference to record |
| Foundation checklist | Anchor bolt template set | Accept / Reject / N/A | Remarks / reference to record |
| Foundation checklist | Concrete/precast element accepted | Accept / Reject / N/A | Remarks / reference to record |
| Foundation checklist | Backfill compacted | Accept / Reject / N/A | Remarks / reference to record |
| Foundation checklist | Site reinstated | Accept / Reject / N/A | Remarks / reference to record |
| Tower checklist | All members present | Accept / Reject / N/A | Remarks / reference to record |
| Tower checklist | Galvanizing acceptable | Accept / Reject / N/A | Remarks / reference to record |
| Tower checklist | Tower verticality checked | Accept / Reject / N/A | Remarks / reference to record |
| Tower checklist | Bolts tightened | Accept / Reject / N/A | Remarks / reference to record |
| Tower checklist | Step bolts installed | Accept / Reject / N/A | Remarks / reference to record |
| Tower checklist | Anti-climbing device installed | Accept / Reject / N/A | Remarks / reference to record |
| Tower checklist | Danger/name/phase/circuit plates installed | Accept / Reject / N/A | Remarks / reference to record |
| Tower checklist | Earthing connection installed | Accept / Reject / N/A | Remarks / reference to record |
| Tower checklist | Punch list closed | Accept / Reject / N/A | Remarks / reference to record |
| Stringing checklist | Drums accepted | Accept / Reject / N/A | Remarks / reference to record |
| Stringing checklist | Crossing protection installed | Accept / Reject / N/A | Remarks / reference to record |
| Stringing checklist | Rollers/sheaves checked | Accept / Reject / N/A | Remarks / reference to record |
| Stringing checklist | Pulling tension recorded | Accept / Reject / N/A | Remarks / reference to record |
| Stringing checklist | Joints inspected | Accept / Reject / N/A | Remarks / reference to record |
| Stringing checklist | Sag accepted | Accept / Reject / N/A | Remarks / reference to record |
| Stringing checklist | Clipping-in completed | Accept / Reject / N/A | Remarks / reference to record |
| Stringing checklist | Dampers installed | Accept / Reject / N/A | Remarks / reference to record |
| Stringing checklist | Clearances verified | Accept / Reject / N/A | Remarks / reference to record |
| Optical checklist | Drum OTDR accepted | Accept / Reject / N/A | Remarks / reference to record |
| Optical checklist | OPGW/ADSS installed without damage | Accept / Reject / N/A | Remarks / reference to record |
| Optical checklist | Downleads clamped | Accept / Reject / N/A | Remarks / reference to record |
| Optical checklist | Joint boxes sealed | Accept / Reject / N/A | Remarks / reference to record |
| Optical checklist | Splices tested | Accept / Reject / N/A | Remarks / reference to record |
| Optical checklist | ODF terminated | Accept / Reject / N/A | Remarks / reference to record |
| Optical checklist | End-to-end OTDR accepted | Accept / Reject / N/A | Remarks / reference to record |
| Optical checklist | Fibre labelling completed | Accept / Reject / N/A | Remarks / reference to record |
| Optical checklist | Trace files submitted | Accept / Reject / N/A | Remarks / reference to record |
| Commissioning checklist | All tests complete | Accept / Reject / N/A | Remarks / reference to record |
| Commissioning checklist | All permits/approvals complete | Accept / Reject / N/A | Remarks / reference to record |
| Commissioning checklist | As-built drawings submitted | Accept / Reject / N/A | Remarks / reference to record |
| Commissioning checklist | Line patrol complete | Accept / Reject / N/A | Remarks / reference to record |
| Commissioning checklist | Punch list closed | Accept / Reject / N/A | Remarks / reference to record |
| Commissioning checklist | GSE/Employer energisation approval obtained | Accept / Reject / N/A | Remarks / reference to record |
| Commissioning checklist | Switching programme approved | Accept / Reject / N/A | Remarks / reference to record |

# Annex-1 Gogni OHTL Detailed Project

This annex includes the detailed design documentation for the 220 kV double-circuit overhead transmission line “Gogni 1-2”, prepared for the connection of the Gogni Wind Farm 220 kV substation to the 220 kV switchyard of Kokhra 500 Substation. The Contractor shall review and comply with all drawings, technical descriptions, route data, tower schedules, foundation details, conductor/OPGW arrangements, crossing details and construction requirements included in this annex. All construction, installation, testing and commissioning activities shall be carried out in accordance with the approved OHTL Detailed Project, GSE requirements, applicable Georgian regulations and this Specification. In case of any discrepancy between this Specification and the approved OHTL Detailed Project, the Contractor shall immediately notify the Employer and obtain written clarification before proceeding.

| Annex Status | To be attached / included in the Contract document set |
| --- | --- |
| Document Control | Latest Employer-approved revision shall apply |
| Contractual Effect | This Annex forms an integral part of the Electrical Works Specification |
| Responsibility | Contractor shall comply with this Annex and notify any inconsistency before execution |