Technical Specification / Terms of Reference (TOR)

Product: Underground Hermetic Sewage Pumping Station 1+1
(Quantities and capacities are provided in Annex No. 2)

Important Notes:

- The parameters specified in Annex No. 2 represent the required duty point.

- The approximate quantities indicated in Annex No. 2 are estimated values only and do not reflect the exact required quantities.

Technical Requirements

The complete set of underground hermetic sewage pumping stations for each required capacity shall include the following equipment and components:

- 2 units of submersible sewage pumps:

  - Power supply: not less than 220V

  - Motor protection class: IP68

  - Minimum cable length: 10 m

  - Pump casing: stainless steel or coated with corrosion-resistant paint

  - Impeller: stainless steel

  - Grinder – Wherever required

- 1 unit of sewage collection/storage tank:

  - Minimum volume: 280 liters

  - Equipped with a hermetically sealed cover

- 1 unit of control panel equipped with:

  - Signal light indicator and Audible alarm system
(The alarm shall activate in case of pump malfunction, blockage, or abnormal operation.)

- Each pumping station set shall also include all components necessary for proper and reliable operation of the station with the specified characteristics, including but not limited to:

  - Check valves (ball-type preferred)

  - Float switches

  - Activated carbon odor-neutralizing filters

  - Other required accessories and fittings

The pumps, check valves, and other accessories shall be installed inside the tank.

For pumping stations with relatively low flow rate and head, the overall height of the station (tank height) should preferably not exceed 1 meter.

Special Requirements

- In the event of signing a contract with the successful bidder, requests for pumps of different capacities and required quantities will be sent to the supplier via the pre-agreed e-mail address. The delivery period for each order shall commence from the date the notification is sent. Orders may include dozens of pumps or, in certain cases, only 1 or 2 pumps.

- The quantities specified in the Excel file are approximate. The Buyer is not obligated to procure all pumping stations of all listed capacities and/or maintain the quantities indicated in the Excel file. Quantities may be increased or decreased according to the Buyer’s actual requirements.

- It is preferable that the bidder be able to present/show an actual pumping station to the Buyer during the tender evaluation process or provide one sample unit.

- If the bidder is unable to present/show an actual pumping station during the tender evaluation process, submission of photo and video materials is mandatory. Such materials shall clearly demonstrate the appearance, specifications, and operating principles of the pumping station. Failure to provide the relevant photo/video materials may result in disqualification of the bidder’s proposal.

The Bidder Shall Submit the Following Documents During Tender Participation

- Fully completed price list (Annex No. 2) – mandatory;

- Separate Folder for each capacity requested in Excel N2 which will comprise the following:

- Complete list of set components, including detailed descriptions, quantities, and photos of all components for each station capacity;

- Product photo and/or video materials if delivery of 1 sample station is not possible (mandatory from the manufacturer);

- Product drawings (mandatory from the manufacturer);

- Product technical datasheets/passports (mandatory from the manufacturer);

- Other documentation/certificates issued by the manufacturer, including:

  - User manuals

  - Installation instructions

  - Certificate of origin

  - Other relevant documents

- Full bidder details, including company and banking information;

- Document/power of attorney confirming the signing authority of the person authorized to sign the contract;

- Extract from the Register of Entrepreneurial and Non-Entrepreneurial (Non-Commercial) Legal Entities, issued after the announcement date of this electronic tender;

- Information regarding delivery terms, warranty conditions, and payment terms;

- Completed compliance questionnaires which will be uploaded to www.tenders.ge together with the present TOR, unless the bidder has already completed the same questionnaire within the last 1 year.