## Full
Elevator Maintenance Checklist
Performed By: |  |  | Periodicity:
Schedule Date: |  |  | Performance Date:
N | Performance Description | Technical Requirement | Check | Notes/Remarks
1. Preparation works
1.1 | Inform appropriate persons regarding elevator stop and make remarks in log | Tools and PPE should be chosen properly, for this type of works.
1.2 | Prepare proper Tools and PPE
2. Checking units on basic level
2.1 | Make sure there is a light on basic level
2.2 | Hang the label "Elevator out of order", with indicating the times -start and finish
2.3 | Make sure all info labels are on the place
2.4 | Check call knobs for proper connection | Knobs shouldn't be damaged and post should be responding
2.5 | Check the Shaft doors of elevators | Shouldn't be visual damages
2.6 | Check the gaps between Shaft doors and frames. | It should be between 2-5 mm
2.7 | Check blocking Contacts of Shaft doors | When force on roller, which opens the Shaft doors and push the move knob on the roof of the cabin, the cabin shouldn't move.
2.8 | Check the gap between Shaft door bottom and floor | It should be between 5+/-1 mm
2.9 | Check display condition | No damages.
3. Check the Elevator Cabin
3.1 | Check cabin for damages and right operation of COP panel. Walls, doors, lights, handrails, floors and glasses if applicable. | No damages. Absence of lights is not allowed.
3.2 | Check the gap between Cabin door bottom and floor | It should be between 5+/-1 mm
3.3 | Check call contact to the dispatcher. | Absent of contact is restricted
3.4 | Check operation of door reverse device | When doors are closing, put something in door opening and doors should be open instantly.
4. Motion of The Cabin on levels
4.1 | Start the cabin by pressing the order buttons on the each floor and make sure the COP panel operates correctly and traveling is comfort | The cabin should come to that floor, where it was requested. When driving, it should not be jerks and increased noise
4.2 | Check cabin floor alignment to the each level floors. | It should be between +/-5 mm
4.3 | Check serviceability door locks and contacts of the cabin Door. After clicking on one of the level buttons, when the cabin comes in move, try to open the cabin door | When you try to unclasp doors, they do not should be opened, and the cab should not stop.
5. Checking the condition of the equipment of the upper floor and equipment located in the upper part of the shaft
5.1 Preparing for observation
5.1.1 | Checking the emergency- inspection operation panel | Panel status and LED test
5.1.2 | Install the cabin on the upper floor, for access to the roof of the cabin | Access procedures for cab roof
5.1.3 | Cur of the Elevator power | The shutdown procedure and provide Lockout/Tagout procedures.
5.1.4 | Clear Controller and the control panel from dust | The presence of dirt and dust is not allowed
5.1.5 | Check fastening of wires in the controller, reliability of electrical contacts to the electric motor | If necessary tighten contacts
5.1.6 | Check for smooth movable of mechanical parts of power contactors and relays when you turn them on by hand, when the power is off | Moving parts movement should be easy, without jamming
5.1.7 | Check manual release mode | Activate both buttons of Manual release, with key.
5.1.8 | Replacing the filter
5.1.9 | Replacing the battery |  |  | Ones in 3 years
5.2 Winch check
5.2.1 | Check fastening drive | If necessary tighten
5.2.2 | Check winch and frame | Mechanical damages are not allowed
5.2.3 | Clear the winch and frame from dust | The presence of dust and dirt does not
5.2.4 | Check fastening of wires in the controller, reliability of electrical contacts to the electric motor | If necessary tighten contacts
5.2.5 | Check breaking devices | Mechanical damages are not allowed
5.3 Checking the speed limit device
5.3.1 | Clean the speed limit device from dust | The presence of dust and dirt does not
5.3.2 | Remove casing from speed limiter and remove dirt from the shaft | The presence of dust and dirt does not
5.3.3 | Check by visual inspection condition of parts and elements of the speed limit device. | Chipped, cracked, breakage, corrosion - not are allowed
5.3.4 | Check creek wear speed limit device | Worn creek before planting rope to the bottom is not allowed
5.3.5 | Checking working condition of Speed limit device | When overspeed the cabin should seat on emergency catch breakers
5.3.6 | Check a regulation of speed limit device
5.4 Inspection of the closing of the traction belts
5.4.1 | Clean the traction belts and hardware from dust and dirt | The presence of dust and dirt does not allowed
5.4.2 | Check status of constituent parts of traction belts and their hardware | Mechanical damages are restricted. fastening should be tightened.
5.5 Checking the operation of the winch
5.5.1 | Produce a trial start of the elevator in one and another direction in mode "Manage from machine room "
5.5.2 | Check working of winches | The winch should work smoothly without vibration and strikes
5.6 Check the end switch
5.6.1 | Clear the end switch from dust and mud | The switch should be working clearly
5.6.2 | Check roller interaction end switch with by layers installed in shaft | Switching the lever should be produced easily, without impact
5.7 Inspection of traction belts and speed limiter rope
5.7.1 | Perform an inspection traction belts, rope speed limiter and their fastening for dirt, mechanical damage and wear. Inspection of traction belts and rope of the limiter speed to produce sequencly | Presence of dirt on the draft out belts, rope speed limiter and their attachment is not allowed Must not be mechanical wear and tear damages
5.7.2 | Check equally tension of traction belts
5.7.3 | Checking alignment of traction belts on pulleys counterweight in the central parts of the mine
5.8. Checking the status of wires and el. System grounding
5.8.1 | Checking of system | Wires must not have breaks of insulation and breakage. Cable sagging is not allowed
6. Checking the cab roof equipment from the floor area
6.1 | Install the cabin in convenient place to enter so that its roof was not more than 200 mm from the floor level sites
6.2 | Open Shaft Door and Install Sliding emphasis. Check serviceability of the roof and hatch external inspection. Check serviceability lighting in the Shaft, clearness on the roof of the cabin | Illumination of mine should be sufficient The presence of mud on the roof cab is not allowed
6.3 | Perform procedure to getting on the roof of the cabin
6.4 Inspection of the cab suspension
6.4.1 | Clean the suspension
6.4.2 | Check the status components of the suspension and their fastening | Mechanical damage is not allowed, fastenings must be tightened.
6.5 Checking the door drive equipment
6.5.1 | Clean compound Parts and components from dirt and dust | The presence of dust and dirt does not allowed
6.5.2 | Check status drive, fastening of rails, rollers to the carriages, leaflets to the carriages and tension communication rope | Mechanical damage, breakage - not allowed
6.5.3 | Check fastening electric motor, reducer, stops, rollers, rulers and other details opening of door leaves cabins | Loose fastening - not allowed
6.5.4 | Check the tension of a belt of a drive of doors | The total value Deflection should not be more than 6 mm
6.5.5 | Check the value of gap between the side separation surfaces cab doors and roller surfaces of the Shaft door lock | The gap at approach to the lock should be 8 ± 1 mm
6.5.6 | Check the clearance between mine threshold and movable cabin platform | The size of the gap must be 9 ± 1.5 mm
6.5.7 | Perform an inspection and check the action of the contact of cabin door
6.6 Checking the condition of the upper beam of the mine door
6.6.1 | Clear equipment (rulers, rollers, counter-shoots, latches, switches, etc.) from dust and dirt | The presence of dust and dirt does not allowed
6.6.2 | Check the clearances between the rulers and counter-carriages door leaves | Gap size is controlled by the feeler gauge and should not exceed 0.2 mm
6.6.3 | Check the clearances between the portal focus and portal focus and lock latch | The gap must be within 2 ÷ 2.5 mm
6.6.4 | Check fastening guide rulers, rollers to the carriages, leaflets to the carriages, shoes | If necessary tighten fasteners
6.6.5 | Check working of shaft door lock contact | When exposed to unlocking roller The doors of the shaft and when you press the buttons on the roof cabin, cabin is not comes into motion
6.7 Inspection of the upper shoe of the cab
6.7.1 | Clean shoes from dirt and dust | The presence of dust and dirt does not
6.7.2 | Perform an inspection shoes | Mechanical damage is not are allowed. Check the force tightening bolts fastening blocks roller shoes (59 +/- 5 Nm). Check installation the size of the springs of all 3 rollers. Size = 31 mm.
6.7.3 | Check the wear rollers | In case if wear - replace
6.8 Checking the condition of the catchers
6.8.1 | Produce visual inspection of catchers | The availability and integrity of all elements
6.8.2 | Check the operation of the safety device
6.8.3 | Check action of lock contact breaker switch. Checking to produce manual lifting of the lever catchers | Check inability to start elevator at operation breaker switch
7. Inspection of equipment in the mine in the mode of "AUDIT"
7.1 | Check top beam of Shaft doors at all floors, except the first, in accordance with paragraph 6.5
7.2 | Check status electrical contacts in devices installed in the shaft and in the cab | Contaminated contact surfaces clear
7.3 | Check the value clearance between sensors read head installed on the cab, and magnets installed on the tape in the Shaft. | The gap should be 3 ± 1 mm
8. Checking the cab guides and counterweight
8.1 | Произвести визуальный осмотр направляющих | In case of detection warp guides, it is necessary to weaken clamping of clamps brackets; then the guide should align. Tighten bolts
8.2 | Clean the guides from dirt and dust | The presence of dust and dirt does not
8.3 | Check by automatic guide rails and counterweight
8.4 | Tighten fasteners guides in the joints
9. Inspection of the counterweight
9.1 | Perform an inspection constituent parts counterweight | Mechanical damage is not are allowed.
9.2 | Check condition of fasteners | All bolts and nuts must be tighten
9.3 | Check shoes counterweight | Same as 6.6
10. Inspection of electric wiring
10.1 | Check condition of wiring and power components. | Wires and cables should not have a broken insulation or breakages The breakers, contactors and connectors shoukld be checked for overheating.
11. Inspection of the equipment of the pit and the floor of the cabin
11.1 Preparation works
11.1.1 | Install the cabin in the second floor zone in an accurate stopping
11.1.2 | Open the Shaft door first floor and lock up sliding stop. Check that the lift is not working to "Call". Check pit lighting
11.1.3 | Switch off the switch of the pit. Enter the pit. Turn on the portable lamp if lighting is not enough. Bring a ladder to the pit | Procedure to enter the pit
11.1.4 | Install the ladder. Climb the stairs. Fasten the safety belt to the brackets of the guides and proceed to inspect the floor of the cabin and the upper beam of the ground floor Shaft door
11.2 Inspection of the suspension cable fixing
11.2.1 | Check status fastening of suspension cable | Cable must not have damage. Mountings should be tightened
11.3 Inspection of low shoes of cabin
11.3.1 | Perform inspection works of low shoes of cabin | Same as 6.6
11.4 Inspection of the upper beam of the mine door of the main landing floor
11.4.1 | Perform inspection works on the upper beam main shaft doors a landing floor, similarly to item 6.5
11.5 Inspection of pit equipment
11.5.1 | Clear the floor of the pit, the buffer, the device of tension rope and speed limiter from dust and dust
11.5.2 | Examine the tensioner of the speed limiter rope, if necessary tighten the fastenings | Elements of tension devices should not have mechanical damages
11.5.3 | Lubricate the hinges speed limiter robe tensioner | According to manual
11.5.4 | Perform an inspection cab buffers and counterweigh | Buffers should not have residual deformations and cracks
11.5.5 | Check oil level (hydraulic buffers) | Must not be leakage of oil
11.5.6 | Check the clearance between the switch roller and adjusting bolt (for hydraulic buffers) | Adjust the setting of the movable frame by tightening the cable or adjusting bolt
11.5.7 | Check the output of the stick. (at the hydraulic buffer) after removal of the load after landing cab (counterweight). | After removing the load The stick should return to initial position
11.5.8 | Check by visual inspection condition of electric devices, wires and cables, their fixing and grounding | The violation of insulation is not allowed
12. Check elevator for operation
13. To remove the poster "Elevator on repair". Record in the log book about the current repair and return the Elevator in operation.

## Monthly
Preventive Maintenance Checklist for Elevators EL-01
Report Form
Performed By: |  |  | Periodicity: Monthly
Unit ID: |  |  | Performing duration:
Unit Serial No: |  |  | Date of service:
N | Performance Description | Technical Requirement | Check | Notes/Remarks
1. Preparation works
1.1 | Inform appropriate persons regarding elevator stop and make remarks in log | Tools and PPE should be chosen properly, for this type of works. | □
1.2 | Prepare proper Tools and PPE |  | □
2. Checking units on basic level
2.1 | Make sure there is a light on basic level |  | □
2.2 | Hang the label "Elevator out of order", with indicating the times -start and finish |  | □
2.3 | Make sure all info labels are on the place |  | □
2.4 | Check call knobs for proper connection | Knobs shouldn't be damaged and post should be responding | □
2.5 | Check the Shaft doors of elevators | Shouldn't be visual damages | □
2.6 | Check the gaps between Shaft doors and frames. | It should be between 2-5 mm | □
2.9 | Check display condition | No damages. | □
3. Check the Elevator Cabin
3.1 | Check cabin for damages and right operation of COP panel. Walls, doors, lights, handrails, floors and glasses if applicable. | No damages. Absence of lights is not allowed. | □
3.2 | Check the gap between Cabin door bottom and floor | It should be between 5+/-1 mm | □
3.3 | Check call contact to the dispatcher. | Absent of contact is restricted | □
3.4 | Check operation of door reverse device | When doors are closing, put something in door opening and doors should be open instantly. | □
4. Motion of The Cabin on levels
4.1 | Start the cabin by pressing the order buttons on the each floor and make sure the COP panel operates correctly and traveling is comfort | The cabin should come to that floor, where it was requested. When driving, it should not be jerks and increased noise | □
4.2 | Check cabin floor alignment to the each level floors. | It should be between +/-5 mm | □
4.3 | Check serviceability door locks and contacts of the cabin Door. After clicking on one of the level buttons, when the cabin comes in move, try to open the cabin door | When you try to unclasp doors, they do not should be opened, and the cab should not stop. | □
4.4 | Check the condition of the door leads of the Shaft, the calling posts and the regulated gaps on each floor in accordance with cl. 2.4-2.8 |  | □
5. Checking the condition of the equipment of the upper floor and equipment located in the upper part of the shaft
5.1 Preparing for observation
5.1.1 | Checking the emergency- inspection operation panel | Panel status and LED test | □
6. Checking the cab roof equipment from the floor area
6.5 Checking the door drive equipment
6.5.7 | Perform an inspection and check the action of the contact of cabin door |  | □
6.6 Checking the condition of the upper beam of the mine door
6.6.5 | Check working of shaft door lock contact | When exposed to unlocking roller The doors of the shaft and when you press the buttons on the roof cabin, cabin is not comes into motion | □
12. Check elevator for operation |  |  | □
13. To remove the poster "Elevator on repair". Record in the log book about the current repair and return the Elevator in operation. |  |  | □
Safety procedures:
1. Lockout/tagout the unit electrical, flammable and mechanical source;
გამოირთოს და ჩაიკეტოს ყველა ელექტრო, აალებადი და მექანიკური მიწოდებები;
2. Use proper PPE (Personal Protective Equipment): Gloves, Goggles, helmet, Safety boots, safety bel for work higher than 1.8m, Noise protection earplugs.
გამოყენებული უნდა იქნას სათანადო პდს (პერსონალური დაცვის საშუალებები): ხელთათმანები, დამცავი სათვალეები, ჩაფხუტი, დაცული ფეხსაცმელი, უსაფრთხოების ქამრები 1.8მ–ზე მაღალ სიმაღლეებზე მუშაობისას, ხმაურის საწინააღმდეგო ყურსაცობი.
3. Make sure maintained area floor is not slippery.
სამუშაო ადგილზე იატაკი არ უნდა იყოს სრიალა
4. Use special protective equipment for hard to access and confined spaces work locations. Decided by safety manager;
გამოყენებული უნდა იყოს სპეციალური პდს (პერსონალური დაცვის საშუალებები) ძნელად შესაღწევ და შეზრუდულ არეაში მუშაობის დროს. გადაწყვეტილება მიიღება შრომის უსაფრთხოების მენეჯერის მიერ.
5. Make sure all tools are in proper condition.
დარწმუნდით, რომ ყველა ინსტრუმენტი კარგ კონდიციაშია
6. Use proper PPE for work locations by thermal and combustion air.
გამოყენებული უნდა იქნას სათანადო პდს (პერსონალური დაცვის საშუალებები) სადაც ხდება თერმიული პროცესები.
Tools and equipment
1. Mechanical set of tools; /მექანიკური ინსტრუმენტების ნაკრები.
2. Cleaning rags and solutions; /საწმენდი ნაჭრები და საშუალებები
3. Vacuum cleaner; /მტვერსასრუტი
4. Proper size ladder (if need); კიბე (თუ საჭიროებაა)
5. Power Tester; დენის ტესტერი
6. Lubricants; საპოხი მასალები
7. Gaps measuring tool; ღრეჩოების საზომი
8. Analyzing tool; ანალიზატორი
Repair works to be performed/ საჭირო სარემონტო სამუშაოების ჩამონათვალი : 1)
| Vertical Transport Engineer : Paata Pataridze |  | ___________________________
| Performer: |  | ___________________________

## Quarterly
Preventive Maintenance Checklist for Elevators EL-03
Report Form
Performed By: |  |  | Periodicity: Quarterly
Unit ID: |  |  | Performing duration:
Unit Serial No: |  |  | Date of service:
N | Performance Description | Technical Requirement | Check | Notes/Remarks
1. Preparation works
1.1 | Inform appropriate persons regarding elevator stop and make remarks in log | Tools and PPE should be chosen properly, for this type of works. | □
1.2 | Prepare proper Tools and PPE |  | □
2. Checking units on basic level
2.1 | Make sure there is a light on basic level |  | □
2.2 | Hang the label "Elevator out of order", with indicating the times -start and finish |  | □
2.3 | Make sure all info labels are on the place |  | □
2.4 | Check call knobs for proper connection | Knobs shouldn't be damaged and post should be responding | □
2.5 | Check the Shaft doors of elevators | Shouldn't be visual damages | □
2.6 | Check the gaps between Shaft doors and frames. | It should be between 2-5 mm | □
2.9 | Check display condition | No damages. | □
3. Check the Elevator Cabin
3.1 | Check cabin for damages and right operation of COP panel. Walls, doors, lights, handrails, floors and glasses if applicable. | No damages. Absence of lights is not allowed. | □
3.2 | Check the gap between Cabin door bottom and floor | It should be between 5+/-1 mm | □
3.3 | Check call contact to the dispatcher. | Absent of contact is restricted | □
3.4 | Check operation of door reverse device | When doors are closing, put something in door opening and doors should be open instantly. | □
4. Motion of The Cabin on levels
4.1 | Start the cabin by pressing the order buttons on the each floor and make sure the COP panel operates correctly and traveling is comfort | The cabin should come to that floor, where it was requested. When driving, it should not be jerks and increased noise | □
4.2 | Check cabin floor alignment to the each level floors. | It should be between +/-5 mm | □
4.3 | Check serviceability door locks and contacts of the cabin Door. After clicking on one of the level buttons, when the cabin comes in move, try to open the cabin door | When you try to unclasp doors, they do not should be opened, and the cab should not stop. | □
4.4 | Check the condition of the door leads of the Shaft, the calling posts and the regulated gaps on each floor in accordance with cl. 2.4-2.8 |  | □
5. Checking the condition of the equipment of the upper floor and equipment located in the upper part of the shaft
5.1 Preparing for observation
5.1.1 | Checking the emergency- inspection operation panel | Panel status and LED test | □
5.1.2 | Install the cabin on the upper floor, for access to the roof of the cabin | Access procedures for cab roof | □
5.1.3 | Cut the Elevator power | The shutdown procedure and provide Lockout/Tag out procedures. | □
5.1.4 | Clear Controller and the control panel from dust | The presence of dirt and dust is not allowed | □
5.5 Checking the operation of the winch
5.5.1 | Produce a trial start of the elevator in one and another direction in mode "Manage from machine room " |  | □
5.5.2 | Check working of winches | The winch should work smoothly without vibration and strikes | □
6. Checking the cab roof equipment from the floor area
6.5 Checking the door drive equipment
6.5.7 | Perform an inspection and check the action of the contact of cabin door |  | □
6.6 Checking the condition of the upper beam of the mine door
6.6.5 | Check working of shaft door lock contact | When exposed to unlocking roller The doors of the shaft and when you press the buttons on the roof cabin, cabin is not comes into motion | □
12. Check elevator for operation |  |  | □
13. To remove the poster "Elevator on repair". Record in the log book about the current repair and return the Elevator in operation. |  |  | □
Safety procedures:
1. Lockout/tagout the unit electrical, flammable and mechanical source;
გამოირთოს და ჩაიკეტოს ყველა ელექტრო, აალებადი და მექანიკური მიწოდებები;
2. Use proper PPE (Personal Protective Equipment): Gloves, Goggles, helmet, Safety boots, safety bel for work higher than 1.8m, Noise protection earplugs.
გამოყენებული უნდა იქნას სათანადო პდს (პერსონალური დაცვის საშუალებები): ხელთათმანები, დამცავი სათვალეები, ჩაფხუტი, დაცული ფეხსაცმელი, უსაფრთხოების ქამრები 1.8მ–ზე მაღალ სიმაღლეებზე მუშაობისას, ხმაურის საწინააღმდეგო ყურსაცობი.
3. Make sure maintained area floor is not slippery.
სამუშაო ადგილზე იატაკი არ უნდა იყოს სრიალა
4. Use special protective equipment for hard to access and confined spaces work locations. Decided by safety manager;
გამოყენებული უნდა იყოს სპეციალური პდს (პერსონალური დაცვის საშუალებები) ძნელად შესაღწევ და შეზრუდულ არეაში მუშაობის დროს. გადაწყვეტილება მიიღება შრომის უსაფრთხოების მენეჯერის მიერ.
5. Make sure all tools are in proper condition.
დარწმუნდით, რომ ყველა ინსტრუმენტი კარგ კონდიციაშია
6. Use proper PPE for work locations by thermal and combustion air.
გამოყენებული უნდა იქნას სათანადო პდს (პერსონალური დაცვის საშუალებები) სადაც ხდება თერმიული პროცესები.
Tools and equipment
1. Mechanical set of tools; /მექანიკური ინსტრუმენტების ნაკრები.
2. Cleaning rags and solutions; /საწმენდი ნაჭრები და საშუალებები
3. Vacuum cleaner; /მტვერსასრუტი
4. Proper size ladder (if need); კიბე (თუ საჭიროებაა)
5. Power Tester; დენის ტესტერი
6. Lubricants; საპოხი მასალები
7. Gaps measuring tool; ღრეჩოების საზომი
8. Analyzing tool; ანალიზატორი
Repair works to be performed/ საჭირო სარემონტო სამუშაოების ჩამონათვალი : 1)
Vertical Transport Engineer : Paata Pataridze |  | ___________________________
Performer |  | ___________________________

## Semiannual
Preventive Maintenance Checklist for Elevators EL-06
Report Form
Performed By: |  |  | Periodicity: Semi Annual
Unit ID: |  |  | Performing duration:
Unit Serial No: |  |  | Date of service:
1. Preparation works
1.1 | Inform appropriate persons regarding elevator stop and make remarks in log | Tools and PPE should be chosen properly, for this type of works. | □
1.2 | Prepare proper Tools and PPE
2. Checking units on basic level
2.1 | Make sure there is a light on basic level |  | □
2.2 | Hang the label "Elevator out of order", with indicating the times -start and finish
2.3 | Make sure all info labels are on the place
2.4 | Check call knobs for proper connection | Knobs shouldn't be damaged and post should be responding
2.5 | Check the Shaft doors of elevators | Shouldn't be visual damages
2.6 | Check the gaps between Shaft doors and frames. | It should be between 2-5 mm
2.7 | Check blocking Contacts of Shaft doors | When force on roller, which opens the Shaft doors and push the move knob on the roof of the cabin, the cabin shouldn't move.
2.8 | Check the gap between Shaft door bottom and floor | It should be between 5+/-1 mm
2.9 | Check display condition | No damages.
3. Check the Elevator Cabin
3.1 | Check cabin for damages and right operation of COP panel. Walls, doors, lights, handrails, floors and glasses if applicable. | No damages. Absence of lights is not allowed. | □
3.2 | Check the gap between Cabin door bottom and floor | It should be between 5+/-1 mm
3.3 | Check call contact to the dispatcher. | Absent of contact is restricted
3.4 | Check operation of door reverse device | When doors are closing, put something in door opening and doors should be open instantly.
4. Motion of The Cabin on levels
4.1 | Start the cabin by pressing the order buttons on the each floor and make sure the COP panel operates correctly and traveling is comfort | The cabin should come to that floor, where it was requested. When driving, it should not be jerks and increased noise | □
4.2 | Check cabin floor alignment to the each level floors. | It should be between +/-5 mm
4.3 | Check serviceability door locks and contacts of the cabin Door. After clicking on one of the level buttons, when the cabin comes in move, try to open the cabin door | When you try to unclasp doors, they do not should be opened, and the cab should not stop.
4.4 | Check the condition of the door leads of the Shaft, the calling posts and the regulated gaps on each floor in accordance with cl. 2.4-2.8
5. Checking the condition of the equipment of the upper floor and equipment located in the upper part of the shaft
5.1 Preparing for observation
5.1.1 | Checking the emergency- inspection operation panel | Panel status and LED test | □
5.1.2 | Install the cabin on the upper floor, for access to the roof of the cabin | Access procedures for cab roof
5.1.3 | Cut the Elevator power | The shutdown procedure and provide Lockout/Tag out procedures.
5.1.4 | Clear Controller and the control panel from dust | The presence of dirt and dust is not allowed
5.1.5 | Check fastening of wires in the controller, reliability of electrical contacts to the electric motor | If necessary tighten contacts
5.1.6 | Check for smooth movable of mechanical parts of power contactors and relays when you turn them on by hand, when the power is off | Moving parts movement should be easy, without jamming
5.2 Winch check
5.2.1 | Check fastening drive | If necessary tighten | □
5.2.2 | Check winch and frame | Mechanical damages are not allowed
5.2.3 | Clear the winch and frame from dust | The presence of dust and dirt does not
5.2.4 | Check fastening of wires in the controller, reliability of electrical contacts to the electric motor | If necessary tighten contacts
5.3 Checking the speed limit device
5.3.1 | Clean the speed limit device from dust | The presence of dust and dirt does not
5.3.2 | Remove casing from speed limiter and remove dirt from the shaft | The presence of dust and dirt does not
5.3.3 | Check by visual inspection condition of parts and elements of the speed limit device. | Chipped, cracked, breakage, corrosion - not are allowed
5.3.4 | Check creek wear speed limit device | Worn creek before planting rope to the bottom is not allowed
5.4 Inspection of the closing of the traction belts
5.4.1 | Clean the traction belts and hardware from dust and dirt | The presence of dust and dirt does not allowed | □
5.4.2 | Check status of constituent parts of traction belts and their hardware | Mechanical damages are restricted. fastening should be tightened.
5.5 Checking the operation of the winch
5.5.1 | Produce a trial start of the elevator in one and another direction in mode "Manage from machine room " |  | □
5.5.2 | Check working of winches | The winch should work smoothly without vibration and strikes
5.6 Check the end switch
5.6.1 | Clear the end switch from dust and mud | The switch should be working clearly
5.6.2 | Check roller interaction end switch with by layers installed in shaft | Switching the lever should be produced easily, without impact
5.7 Inspection of traction belts and speed limiter rope
5.7.1 | Perform an inspection traction belts, rope speed limiter and their fastening for dirt, mechanical damage and wear. Inspection of traction belts and rope of the limiter speed to produce successively | Presence of dirt on the draft out belts, rope speed limiter and their attachment is not allowed Must not be mechanical wear and tear damages
6. Checking the cab roof equipment from the floor area
6.1 | Install the cabin in convenient place to enter so that its roof was not more than 200 mm from the floor level sites |  | □
6.2 | Open Shaft Door and Install Sliding emphasis. Check serviceability of the roof and hatch external inspection. Check serviceability lighting in the Shaft, clearness on the roof of the cabin | Illumination of mine should be sufficient The presence of mud on the roof cab is not allowed
6.3 | Perform procedure to getting on the roof of the cabin
6.4 Inspection of the cab suspension
6.4.1 | Clean the suspension |  | □
6.4.2 | Check the status components of the suspension and their fastening | Mechanical damage is not allowed, fastenings must be tightened.
6.5 Checking the door drive equipment
6.5.1 | Clean compound Parts and components from dirt and dust | The presence of dust and dirt does not allowed | □
6.5.2 | Check status drive, fastening of rails, rollers to the carriages, leaflets to the carriages and tension communication rope | Mechanical damage, breakage - not allowed
6.5.3 | Check fastening electric motor, reducer, stops, rollers, rulers and other details opening of door leaves cabins | Loose fastening - not allowed
6.5.4 | Check the tension of a belt of a drive of doors | The total value Deflection should not be more than 6 mm
6.5.5 | Check the value of gap between the side separation surfaces cab doors and roller surfaces of the Shaft door lock | The gap at approach to the lock should be 8 ± 1 mm
6.5.6 | Check the clearance between mine threshold and movable cabin platform | The size of the gap must be 9 ± 1.5 mm
6.5.7 | Perform an inspection and check the action of the contact of cabin door
6.6 Checking the condition of the upper beam of the mine door
6.6.1 | Clear equipment (rulers, rollers, counter-shoots, latches, switches, etc.) from dust and dirt | The presence of dust and dirt does not allowed | □
6.6.2 | Check the clearances between the rulers and counter-carriages door leaves | Gap size is controlled by the feeler gauge and should not exceed 0.2 mm
6.6.3 | Check the clearances between the portal focus and portal focus and lock latch | The gap must be within 2 ÷ 2.5 mm
6.6.4 | Check fastening guide rulers, rollers to the carriages, leaflets to the carriages, shoes | If necessary tighten fasteners
6.6.5 | Check working of shaft door lock contact | When exposed to unlocking roller The doors of the shaft and when you press the buttons on the roof cabin, cabin is not comes into motion
6.7 Inspection of the upper shoe of the cab
6.7.1 | Clean shoes from dirt and dust | The presence of dust and dirt does not | □
6.7.2 | Perform an inspection shoes | Mechanical damage is not are allowed. Check the force tightening bolts fastening blocks roller shoes (59 +/- 5 Nm). Check installation the size of the springs of all 3 rollers. Size = 31 mm.
6.7.3 | Check the wear rollers | In case if wear - replace
6.8 Checking the condition of the catchers
6.8.1 | Produce visual inspection of catchers | The availability and integrity of all elements | □
6.8.2 | Check the operation of the safety device
6.8.3 | Check action of lock contact breaker switch. Checking to produce manual lifting of the lever catchers | Check inability to start elevator at operation breaker switch
7. Inspection of equipment in the mine in the mode of "AUDIT"
7.1 | Check top beam of Shaft doors at all floors, except the first, in accordance with paragraph 6.5
7.2 | Check status electrical contacts in devices installed in the shaft and in the cab | Contaminated contact surfaces clear
7.3 | Check the value clearance between sensors read head installed on the cab, and magnets installed on the tape in the Shaft. | The gap should be 3 ± 1 mm
8. Checking the cab guides and counterweight
8.1 | Произвести визуальный осмотр направляющих | In case of detection warp guides, it is necessary to weaken clamping of clamps brackets; then the guide should align. Tighten bolts | □
8.2 | Clean the guides from dirt and dust | The presence of dust and dirt does not
8.3 | Check by automatic guide rails and counterweight
8.4 | Tighten fasteners guides in the joints
9. Inspection of the counterweight
9.1 | Perform an inspection constituent parts counterweight | Mechanical damage is not are allowed. | □
9.2 | Check condition of fasteners | All bolts and nuts must be tighten
9.3 | Check shoes counterweight | Same as 6.6
10. Inspection of electric wiring
10.1 | Check condition of wiring and power components. | Wires and cables should not have a broken insulation or breakages The breakers, contactors and connectors shoukld be checked for overheating. | □
11. Inspection of the equipment of the pit and the floor of the cabin
11.1 Preparation works |  |  | □
11.1.1 | Install the cabin in the second floor zone in an accurate stopping
11.1.2 | Open the Shaft door first floor and lock up sliding stop. Check that the lift is not working to "Call". Check pit lighting
11.1.3 | Switch off the switch of the pit. Enter the pit. Turn on the portable lamp if lighting is not enough. Bring a ladder to the pit | Procedure to enter the pit
11.1.4 | Install the ladder. Climb the stairs. Fasten the safety belt to the brackets of the guides and proceed to inspect the floor of the cabin and the upper beam of the ground floor Shaft door
11.2 Inspection of the suspension cable fixing
11.2.1 | Check status fastening of suspension cable | Cable must not have damage. Mountings should be tightened | □
11.3 Inspection of low shoes of cabin
11.3.1 | Perform inspection works of low shoes of cabin | Same as 6.6 | □
11.4 Inspection of the upper beam of the mine door of the main landing floor
11.4.1 | Perform inspection works on the upper beam main shaft doors a landing floor, similarly to item 6.5 |  | □
11.5 Inspection of pit equipment
11.5.1 | Clear the floor of the pit, the buffer, the device of tension rope and speed limiter from dust and dust |  | □
11.5.2 | Examine the tensioner of the speed limiter rope, if necessary tighten the fastenings | Elements of tension devices should not have mechanical damages
11.5.3 | Lubricate the hinges speed limiter robe tensioner | According to manual
11.5.4 | Perform an inspection cab buffers and counterweigh | Buffers should not have residual deformations and cracks
11.5.5 | Check oil level (hydraulic buffers) | Must not be leakage of oil
11.5.6 | Check the clearance between the switch roller and adjusting bolt (for hydraulic buffers) | Adjust the setting of the movable frame by tightening the cable or adjusting bolt
11.5.8 | Check by visual inspection condition of electric devices, wires and cables, their fixing and grounding | The violation of insulation is not allowed
12. Check elevator for operation
13. To remove the poster "Elevator on repair". Record in the log book about the current repair and return the Elevator in operation. |  |  | □
Safety procedures:
1. Lockout/tagout the unit electrical, flammable and mechanical source;
გამოირთოს და ჩაიკეტოს ყველა ელექტრო, აალებადი და მექანიკური მიწოდებები;
2. Use proper PPE (Personal Protective Equipment): Gloves, Goggles, helmet, Safety boots, safety bel for work higher than 1.8m, Noise protection earplugs.
გამოყენებული უნდა იქნას სათანადო პდს (პერსონალური დაცვის საშუალებები): ხელთათმანები, დამცავი სათვალეები, ჩაფხუტი, დაცული ფეხსაცმელი, უსაფრთხოების ქამრები 1.8მ–ზე მაღალ სიმაღლეებზე მუშაობისას, ხმაურის საწინააღმდეგო ყურსაცობი.
3. Make sure maintained area floor is not slippery.
სამუშაო ადგილზე იატაკი არ უნდა იყოს სრიალა
4. Use special protective equipment for hard to access and confined spaces work locations. Decided by safety manager;
გამოყენებული უნდა იყოს სპეციალური პდს (პერსონალური დაცვის საშუალებები) ძნელად შესაღწევ და შეზრუდულ არეაში მუშაობის დროს. გადაწყვეტილება მიიღება შრომის უსაფრთხოების მენეჯერის მიერ.
5. Make sure all tools are in proper condition.
დარწმუნდით, რომ ყველა ინსტრუმენტი კარგ კონდიციაშია
6. Use proper PPE for work locations by thermal and combustion air.
გამოყენებული უნდა იქნას სათანადო პდს (პერსონალური დაცვის საშუალებები) სადაც ხდება თერმიული პროცესები.
Tools and equipment
1. Mechanical set of tools; /მექანიკური ინსტრუმენტების ნაკრები.
2. Cleaning rags and solutions; /საწმენდი ნაჭრები და საშუალებები
3. Vacuum cleaner; /მტვერსასრუტი
4. Proper size ladder (if need); კიბე (თუ საჭიროებაა)
5. Power Tester; დენის ტესტერი
6. Lubricants; საპოხი მასალები
7. Gaps measuring tool; ღრეჩოების საზომი
8. Analyzing tool; ანალიზატორი
Repair works to be performed/ საჭირო სარემონტო სამუშაოების ჩამონათვალი : 1)
Vertical Transport Engineer : Paata Pataridze |  | ___________________________
Performer: |  | ___________________________

## Annual
Preventive Maintenance Checklist for Elevators EL-12
Report Form
Performed By: |  |  | Periodicity: Annual
Unit ID: |  |  | Performing duration:
Unit Serial No: |  |  | Date of service:
N | Performance Description | Technical Requirement | Check | Notes/Remarks
1. Preparation works
1.1 | Inform appropriate persons regarding elevator stop and make remarks in log | Tools and PPE should be chosen properly, for this type of works. | □
1.2 | Prepare proper Tools and PPE |  | □
2. Checking units on basic level
2.1 | Make sure there is a light on basic level |  | □
2.2 | Hang the label "Elevator out of order", with indicating the times -start and finish |  | □
2.3 | Make sure all info labels are on the place |  | □
2.4 | Check call knobs for proper connection | Knobs shouldn't be damaged and post should be responding | □
2.5 | Check the Shaft doors of elevators | Shouldn't be visual damages | □
2.6 | Check the gaps between Shaft doors and frames. | It should be between 2-5 mm | □
2.7 | Check blocking Contacts of Shaft doors | When force on roller, which opens the Shaft doors and push the move knob on the roof of the cabin, the cabin shouldn't move. | □
2.8 | Check the gap between Shaft door bottom and floor | It should be between 5+/-1 mm | □
2.9 | Check display condition | No damages. | □
3. Check the Elevator Cabin
3.1 | Check cabin for damages and right operation of COP panel. Walls, doors, lights, handrails, floors and glasses if applicable. | No damages. Absence of lights is not allowed. | □
3.2 | Check the gap between Cabin door bottom and floor | It should be between 5+/-1 mm | □
3.3 | Check call contact to the dispatcher. | Absent of contact is restricted | □
3.4 | Check operation of door reverse device | When doors are closing, put something in door opening and doors should be open instantly. | □
4. Motion of The Cabin on levels
4.1 | Start the cabin by pressing the order buttons on the each floor and make sure the COP panel operates correctly and traveling is comfort | The cabin should come to that floor, where it was requested. When driving, it should not be jerks and increased noise | □
4.2 | Check cabin floor alignment to the each level floors. | It should be between +/-5 mm | □
4.3 | Check serviceability door locks and contacts of the cabin Door. After clicking on one of the level buttons, when the cabin comes in move, try to open the cabin door | When you try to unclasp doors, they do not should be opened, and the cab should not stop. | □
5. Checking the condition of the equipment of the upper floor and equipment located in the upper part of the shaft
5.1 Preparing for observation
5.1.1 | Checking the emergency- inspection operation panel | Panel status and LED test | □
5.1.2 | Install the cabin on the upper floor, for access to the roof of the cabin | Access procedures for cab roof | □
5.1.3 | Cut the Elevator power | The shutdown procedure and provide Lockout/Tagout procedures. | □
5.1.4 | Clear Controller and the control panel from dust | The presence of dirt and dust is not allowed | □
5.1.5 | Check fastening of wires in the controller, reliability of electrical contacts to the electric motor | If necessary tighten contacts | □
5.1.6 | Check for smooth movable of mechanical parts of power contactors and relays when you turn them on by hand, when the power is off | Moving parts movement should be easy, without jamming | □
5.1.7 | Check manual release mode | Activate both buttons of Manual release, with key. | □
5.1.8 | Replacing the filter |  | □
5.1.9 | Replacing the battery |  | □ | Ones in 3 years
5.2 Winch check
5.2.1 | Check fastening drive | If necessary tighten | □
5.2.2 | Check winch and frame | Mechanical damages are not allowed | □
5.2.3 | Clear the winch and frame from dust | The presence of dust and dirt does not | □
5.2.4 | Check fastening of wires in the controller, reliability of electrical contacts to the electric motor | If necessary tighten contacts | □
5.2.5 | Check breaking devices | Mechanical damages are not allowed | □
5.3 Checking the speed limit device
5.3.1 | Clean the speed limit device from dust | The presence of dust and dirt does not | □
5.3.2 | Remove casing from speed limiter and remove dirt from the shaft | The presence of dust and dirt does not | □
5.3.3 | Check by visual inspection condition of parts and elements of the speed limit device. | Chipped, cracked, breakage, corrosion - not are allowed | □
5.3.4 | Check creek wear speed limit device | Worn creek before planting rope to the bottom is not allowed | □
5.3.5 | Checking working condition of Speed limit device | When overspeed the cabin should seat on emergency catch breakers | □
5.3.6 | Check a regulation of speed limit device |  | □
5.4 Inspection of the closing of the traction belts
5.4.1 | Clean the traction belts and hardware from dust and dirt | The presence of dust and dirt does not allowed | □
5.4.2 | Check status of constituent parts of traction belts and their hardware | Mechanical damages are restricted. fastening should be tightened. | □
5.5 Checking the operation of the winch
5.5.1 | Produce a trial start of the elevator in one and another direction in mode "Manage from machine room " |  | □
5.5.2 | Check working of winches | The winch should work smoothly without vibration and strikes | □
5.6 Check the end switch
5.6.1 | Clear the end switch from dust and mud | The switch should be working clearly | □
5.6.2 | Check roller interaction end switch with by layers installed in shaft | Switching the lever should be produced easily, without impact | □
5.7 Inspection of traction belts and speed limiter rope
5.7.1 | Perform an inspection traction belts, rope speed limiter and their fastening for dirt, mechanical damage and wear. Inspection of traction belts and rope of the limiter speed to produce successively | Presence of dirt on the draft out belts, rope speed limiter and their attachment is not allowed Must not be mechanical wear and tear damages | □
5.7.2 | Check equally tension of traction belts |  | □
5.7.3 | Checking alignment of traction belts on pulleys counterweight in the central parts of the mine |  | □
5.8. Checking the status of wires and el. System grounding
5.8.1 | Checking of system | Wires must not have breaks of insulation and breakage. Cable sagging is not allowed | □
6. Checking the cab roof equipment from the floor area
6.1 | Install the cabin in convenient place to enter so that its roof was not more than 200 mm from the floor level sites |  | □
6.2 | Open Shaft Door and Install Sliding emphasis. Check serviceability of the roof and hatch external inspection. Check serviceability lighting in the Shaft, clearness on the roof of the cabin | Illumination of mine should be sufficient The presence of mud on the roof cab is not allowed | □
6.3 | Perform procedure to getting on the roof of the cabin |  | □
6.4 Inspection of the cab suspension
6.4.1 | Clean the suspension |  | □
6.4.2 | Check the status components of the suspension and their fastening | Mechanical damage is not allowed, fastenings must be tightened. | □
6.5 Checking the door drive equipment
6.5.1 | Clean compound Parts and components from dirt and dust | The presence of dust and dirt does not allowed | □
6.5.2 | Check status drive, fastening of rails, rollers to the carriages, leaflets to the carriages and tension communication rope | Mechanical damage, breakage - not allowed | □
6.5.3 | Check fastening electric motor, reducer, stops, rollers, rulers and other details opening of door leaves cabins | Loose fastening - not allowed | □
6.5.4 | Check the tension of a belt of a drive of doors | The total value Deflection should not be more than 6 mm | □
6.5.5 | Check the value of gap between the side separation surfaces cab doors and roller surfaces of the Shaft door lock | The gap at approach to the lock should be 8 ± 1 mm | □
6.5.6 | Check the clearance between mine threshold and movable cabin platform | The size of the gap must be 9 ± 1.5 mm | □
6.5.7 | Perform an inspection and check the action of the contact of cabin door |  | □
6.6 Checking the condition of the upper beam of the mine door
6.6.1 | Clear equipment (rulers, rollers, counter-shoots, latches, switches, etc.) from dust and dirt | The presence of dust and dirt does not allowed | □
6.6.2 | Check the clearances between the rulers and counter-carriages door leaves | Gap size is controlled by the feeler gauge and should not exceed 0.2 mm | □
6.6.3 | Check the clearances between the portal focus and portal focus and lock latch | The gap must be within 2 ÷ 2.5 mm | □
6.6.4 | Check fastening guide rulers, rollers to the carriages, leaflets to the carriages, shoes | If necessary tighten fasteners | □
6.6.5 | Check working of shaft door lock contact | When exposed to unlocking roller The doors of the shaft and when you press the buttons on the roof cabin, cabin is not comes into motion | □
6.7 Inspection of the upper shoe of the cab
6.7.1 | Clean shoes from dirt and dust | The presence of dust and dirt does not | □
6.7.2 | Perform an inspection shoes | Mechanical damage is not are allowed. Check the force tightening bolts fastening blocks roller shoes (59 +/- 5 Nm). Check installation the size of the springs of all 3 rollers. Size = 31 mm. | □
6.7.3 | Check the wear rollers | In case if wear - replace | □
6.8 Checking the condition of the catchers
6.8.1 | Produce visual inspection of catchers | The availability and integrity of all elements | □
6.8.2 | Check the operation of the safety device |  | □
6.8.3 | Check action of lock contact breaker switch. Checking to produce manual lifting of the lever catchers | Check inability to start elevator at operation breaker switch | □
7. Inspection of equipment in the mine in the mode of "AUDIT"
7.1 | Check top beam of Shaft doors at all floors, except the first, in accordance with paragraph 6.5 |  | □
7.2 | Check status electrical contacts in devices installed in the shaft and in the cab | Contaminated contact surfaces clear | □
7.3 | Check the value clearance between sensors read head installed on the cab, and magnets installed on the tape in the Shaft. | The gap should be 3 ± 1 mm | □
8. Checking the cab guides and counterweight
8.1 | Perform a visual inspection of the guides | In case of detection warp guides, it is necessary to weaken clamping of clamps brackets; then the guide should align. Tighten bolts | □
8.2 | Clean the guides from dirt and dust | The presence of dust and dirt does not | □
8.3 | Check by automatic guide rails and counterweight |  | □
8.4 | Tighten fasteners guides in the joints |  | □
9. Inspection of the counterweight
9.1 | Perform an inspection constituent parts counterweight | Mechanical damage is not are allowed. | □
9.2 | Check condition of fasteners | All bolts and nuts must be tighten | □
9.3 | Check shoes counterweight | Same as 6.6 | □
10. Inspection of electric wiring
10.1 | Check condition of wiring and power components. | Wires and cables should not have a broken insulation or breakages The breakers, contactors and connectors shoukld be checked for overheating. | □
11. Inspection of the equipment of the pit and the floor of the cabin
11.1 Preparation works
11.1.1 | Install the cabin in the second floor zone in an accurate stopping |  | □
11.1.2 | Open the Shaft door first floor and lock up sliding stop. Check that the lift is not working to "Call". Check pit lighting |  | □
11.1.3 | Switch off the switch of the pit. Enter the pit. Turn on the portable lamp if lighting is not enough. Bring a ladder to the pit | Procedure to enter the pit | □
11.1.4 | Install the ladder. Climb the stairs. Fasten the safety belt to the brackets of the guides and proceed to inspect the floor of the cabin and the upper beam of the ground floor Shaft door |  | □
11.2 Inspection of the suspension cable fixing
11.2.1 | Check status fastening of suspension cable | Cable must not have damage. Mountings should be tightened | □
11.3 Inspection of low shoes of cabin
11.3.1 | Perform inspection works of low shoes of cabin | Same as 6.6 | □
11.4 Inspection of the upper beam of the mine door of the main landing floor
11.4.1 | Perform inspection works on the upper beam main shaft doors a landing floor, similarly to item 6.5 |  | □
11.5 Inspection of pit equipment
11.5.1 | Clear the floor of the pit, the buffer, the device of tension rope and speed limiter from dust and dust |  | □
11.5.2 | Examine the tensioner of the speed limiter rope, if necessary tighten the fastenings | Elements of tension devices should not have mechanical damages | □
11.5.3 | Lubricate the hinges speed limiter robe tensioner | According to manual | □
11.5.4 | Perform an inspection cab buffers and counterweigh | Buffers should not have residual deformations and cracks | □
11.5.5 | Check oil level (hydraulic buffers) | Must not be leakage of oil | □
11.5.6 | Check the clearance between the switch roller and adjusting bolt (for hydraulic buffers) | Adjust the setting of the movable frame by tightening the cable or adjusting bolt | □
11.5.7 | Check the output of the stick. (at the hydraulic buffer) after removal of the load after landing cab (counterweight). | After removing the load The stick should return to initial position | □
11.5.8 | Check by visual inspection condition of electric devices, wires and cables, their fixing and grounding | The violation of insulation is not allowed | □
12. Check elevator for operation
13. To remove the poster "Elevator on repair". Record in the log book about the current repair and return the Elevator in operation. |  |  | □
Safety procedures:
1. Lockout/tagout the unit electrical, flammable and mechanical source;
გამოირთოს და ჩაიკეტოს ყველა ელექტრო, აალებადი და მექანიკური მიწოდებები;
2. Use proper PPE (Personal Protective Equipment): Gloves, Goggles, helmet, Safety boots, safety bel for work higher than 1.8m, Noise protection earplugs.
გამოყენებული უნდა იქნას სათანადო პდს (პერსონალური დაცვის საშუალებები): ხელთათმანები, დამცავი სათვალეები, ჩაფხუტი, დაცული ფეხსაცმელი, უსაფრთხოების ქამრები 1.8მ–ზე მაღალ სიმაღლეებზე მუშაობისას, ხმაურის საწინააღმდეგო ყურსაცობი.
3. Make sure maintained area floor is not slippery.
სამუშაო ადგილზე იატაკი არ უნდა იყოს სრიალა
4. Use special protective equipment for hard to access and confined spaces work locations. Decided by safety manager;
გამოყენებული უნდა იყოს სპეციალური პდს (პერსონალური დაცვის საშუალებები) ძნელად შესაღწევ და შეზრუდულ არეაში მუშაობის დროს. გადაწყვეტილება მიიღება შრომის უსაფრთხოების მენეჯერის მიერ.
5. Make sure all tools are in proper condition.
დარწმუნდით, რომ ყველა ინსტრუმენტი კარგ კონდიციაშია
6. Use proper PPE for work locations by thermal and combustion air.
გამოყენებული უნდა იქნას სათანადო პდს (პერსონალური დაცვის საშუალებები) სადაც ხდება თერმიული პროცესები.
Tools and equipment
1. Mechanical set of tools; /მექანიკური ინსტრუმენტების ნაკრები.
2. Cleaning rags and solutions; /საწმენდი ნაჭრები და საშუალებები
3. Vacuum cleaner; /მტვერსასრუტი
4. Proper size ladder (if need); კიბე (თუ საჭიროებაა)
5. Power Tester; დენის ტესტერი
6. Lubricants; საპოხი მასალები
7. Gaps measuring tool; ღრეჩოების საზომი
8. Analyzing tool; ანალიზატორი
Repair works to be performed/ საჭირო სარემონტო სამუშაოების ჩამონათვალი : 1)
Vertical Transport Engineer : Paata Pataridze |  | ___________________________
Performer: |  | ___________________________